## Maps
Modbus map | SLAVE LINK 1 : TCP/IP socket 4
PROTOCOL | MODBUS TCP SLAVE
SLAVE NUMBER 1
REGISTER DATA MAP
================
EVENTING MODE :
SECURITY LEVEL :
No. | EVENTING MODE | SECURITY LEVEL | Floboss | SCADA | [5 empty] | Curent Report
1 | CHANGES | READ / WRITE | 47001 | 47002 | PT-12501-01 | MODE |  | Float (MSB 1st) | 4
2 | DISABLED | READ ONLY | 47003 | 47004 |  | INUSE |  | Float (MSB 1st) | 120
3 | CHANGES | READ / WRITE | 47005 | 47006 |  | KEYPAD |  | Float (MSB 1st) | 120
4 | DISABLED | READ ONLY | 47007 | 47008 |  | MEASURED |  | Float (MSB 1st) | -124.9862
5 |  |  | 47009 | 47010 |  | CURRENT |  | Float (MSB 1st) | 0.000443
6 | CHANGES | READ / WRITE | 47011 | 47012 |  | LOSCALE |  | Float (MSB 1st) | 0
7 |  |  | 47013 | 47014 |  | HISCALE |  | Float (MSB 1st) | 500
8 |  |  | 47015 | 47016 |  | HILIM |  | Float (MSB 1st) | 200
9 |  |  | 47017 | 47018 |  | LOLIM |  | Float (MSB 1st) | 60
10 |  |  | 47019 | 47020 | DPT-12501-01 | MODE |  | Float (MSB 1st) | 4
11 | DISABLED | READ ONLY | 47021 | 47022 |  | INUSE |  | Float (MSB 1st) | 0
12 | CHANGES | READ / WRITE | 47023 | 47024 |  | KEYPAD |  | Float (MSB 1st) | 0
13 | DISABLED | READ ONLY | 47025 | 47026 |  | MEASURED |  | Float (MSB 1st) | -49.9937
14 |  |  | 47027 | 47028 |  | CURRENT |  | Float (MSB 1st) | 0.0005
15 | CHANGES | READ / WRITE | 47029 | 47030 |  | LOSCALE |  | Float (MSB 1st) | 0
16 |  |  | 47031 | 47032 |  | HISCALE |  | Float (MSB 1st) | 200
17 |  |  | 47033 | 47034 |  | HILIM |  | Float (MSB 1st) | 200
18 |  |  | 47035 | 47036 |  | LOLIM |  | Float (MSB 1st) | -2
19 |  |  | 47037 | 47038 | TT-12501-01 | MODE |  | Float (MSB 1st) | 4
20 | DISABLED | READ ONLY | 47039 | 47040 |  | INUSE |  | Float (MSB 1st) | 82
21 | CHANGES | READ / WRITE | 47041 | 47042 |  | KEYPAD |  | Float (MSB 1st) | 82
22 | DISABLED | READ ONLY | 47043 | 47044 |  | MEASURED |  | Float (MSB 1st) | -37.4951
23 |  |  | 47045 | 47046 |  | CURRENT |  | Float (MSB 1st) | 0.000524
24 | CHANGES | READ / WRITE | 47047 | 47048 |  | LOSCALE |  | Float (MSB 1st) | 0
25 |  |  | 47049 | 47050 |  | HISCALE |  | Float (MSB 1st) | 150
26 |  |  | 47051 | 47052 |  | HILIM |  | Float (MSB 1st) | 86
27 |  |  | 47053 | 47054 |  | LOLIM |  | Float (MSB 1st) | 75
28 |  |  | 47055 | 47056 | PT-12501-04 | MODE |  | Float (MSB 1st) | 4
29 | DISABLED | READ ONLY | 47057 | 47058 |  | INUSE |  | Float (MSB 1st) | 300
30 | CHANGES | READ / WRITE | 47059 | 47060 |  | KEYPAD |  | Float (MSB 1st) | 300
31 | DISABLED | READ ONLY | 47061 | 47062 |  | MEASURED |  | Float (MSB 1st) | -124.9838
32 |  |  | 47063 | 47064 |  | CURRENT |  | Float (MSB 1st) | 0.000517
33 | CHANGES | READ / WRITE | 47065 | 47066 |  | LOSCALE |  | Float (MSB 1st) | 0
34 |  |  | 47067 | 47068 |  | HISCALE |  | Float (MSB 1st) | 500
35 |  |  | 47069 | 47070 |  | HILIM |  | Float (MSB 1st) | 400
36 |  |  | 47071 | 47072 |  | LOLIM |  | Float (MSB 1st) | 60
37 |  |  | 47073 | 47074 | PT-12501-05 | MODE |  | Float (MSB 1st) | 4
38 | DISABLED | READ ONLY | 47075 | 47076 |  | INUSE |  | Float (MSB 1st) | 200
39 | CHANGES | READ / WRITE | 47077 | 47078 |  | KEYPAD |  | Float (MSB 1st) | 200
40 | DISABLED | READ ONLY | 47079 | 47080 |  | MEASURED |  | Float (MSB 1st) | -124.982
41 |  |  | 47081 | 47082 |  | CURRENT |  | Float (MSB 1st) | 0.000575
42 | CHANGES | READ / WRITE | 47083 | 47084 |  | LOSCALE |  | Float (MSB 1st) | 0
43 |  |  | 47085 | 47086 |  | HISCALE |  | Float (MSB 1st) | 500
44 |  |  | 47087 | 47088 |  | HILIM |  | Float (MSB 1st) | 120
45 |  |  | 47089 | 47090 |  | LOLIM |  | Float (MSB 1st) | 50
46 |  |  | 47091 | 47092 | PT-12501-02 | MODE |  | Float (MSB 1st) | 4
47 | DISABLED | READ ONLY | 47093 | 47094 |  | INUSE |  | Float (MSB 1st) | 120
48 | CHANGES | READ / WRITE | 47095 | 47096 |  | KEYPAD |  | Float (MSB 1st) | 120
49 | DISABLED | READ ONLY | 47097 | 47098 |  | MEASURED |  | Float (MSB 1st) | -124.9825
50 |  |  | 47099 | 47100 |  | CURRENT |  | Float (MSB 1st) | 0.00056
51 | CHANGES | READ / WRITE | 47101 | 47102 |  | LOSCALE |  | Float (MSB 1st) | 0
52 |  |  | 47103 | 47104 |  | HISCALE |  | Float (MSB 1st) | 500
53 |  |  | 47105 | 47106 |  | HILIM |  | Float (MSB 1st) | 200
54 |  |  | 47107 | 47108 |  | LOLIM |  | Float (MSB 1st) | 60
55 |  |  | 47109 | 47110 | DPT-12501-02 | MODE |  | Float (MSB 1st) | 4
56 | DISABLED | READ ONLY | 47111 | 47112 |  | INUSE |  | Float (MSB 1st) | 0
57 | CHANGES | READ / WRITE | 47113 | 47114 |  | KEYPAD |  | Float (MSB 1st) | 0
58 | DISABLED | READ ONLY | 47115 | 47116 |  | MEASURED |  | Float (MSB 1st) | -49.9938
59 |  |  | 47117 | 47118 |  | CURRENT |  | Float (MSB 1st) | 0.000496
60 | CHANGES | READ / WRITE | 47119 | 47120 |  | LOSCALE |  | Float (MSB 1st) | 0
61 |  |  | 47121 | 47122 |  | HISCALE |  | Float (MSB 1st) | 200
62 |  |  | 47123 | 47124 |  | HILIM |  | Float (MSB 1st) | 200
63 |  |  | 47125 | 47126 |  | LOLIM |  | Float (MSB 1st) | -2
64 |  |  | 47127 | 47128 | TT-12501-02 | MODE |  | Float (MSB 1st) | 4
65 | DISABLED | READ ONLY | 47129 | 47130 |  | INUSE |  | Float (MSB 1st) | 82
66 | CHANGES | READ / WRITE | 47131 | 47132 |  | KEYPAD |  | Float (MSB 1st) | 82
67 | DISABLED | READ ONLY | 47133 | 47134 |  | MEASURED |  | Float (MSB 1st) | -37.4938
68 |  |  | 47135 | 47136 |  | CURRENT |  | Float (MSB 1st) | 0.000657
69 | CHANGES | READ / WRITE | 47137 | 47138 |  | LOSCALE |  | Float (MSB 1st) | 0
70 |  |  | 47139 | 47140 |  | HISCALE |  | Float (MSB 1st) | 150
71 |  |  | 47141 | 47142 |  | HILIM |  | Float (MSB 1st) | 86
72 |  |  | 47143 | 47144 |  | LOLIM |  | Float (MSB 1st) | 75
73 | DISABLED | READ ONLY | 47145 | 47146 | STN01 FWD | UVOL | TOTAL {Fiscal Totalizer} | Float (MSB 1st) | 438.5892
74 |  |  | 47147 | 47148 |  | CVOL |  | Float (MSB 1st) | 680.8268
75 |  |  | 47149 | 47150 |  | MASS |  | Float (MSB 1st) | 33.8767
76 |  |  | 47151 | 47152 |  | ENERGY |  | Float (MSB 1st) | 720.5638
77 |  |  | 47153 | 47154 | STR01 FWD | UVOL |  | Float (MSB 1st) | 187.0043
78 |  |  | 47155 | 47156 |  | CVOL |  | Float (MSB 1st) | 301.207
79 |  |  | 47157 | 47158 |  | MASS |  | Float (MSB 1st) | 14.9875
80 |  |  | 47159 | 47160 |  | ENERGY |  | Float (MSB 1st) | 318.7872
81 |  |  | 47161 | 47162 | STR02 FWD | UVOL |  | Float (MSB 1st) | 251.5849
82 |  |  | 47163 | 47164 |  | CVOL |  | Float (MSB 1st) | 379.6198
83 |  |  | 47165 | 47166 |  | MASS |  | Float (MSB 1st) | 18.8892
84 |  |  | 47167 | 47168 |  | ENERGY |  | Float (MSB 1st) | 401.7766
85 |  |  | 47169 | 47170 | STN01 FWD | UVOL HOURLY | PREVIOUS {Fiscal Hourly} | Float (MSB 1st) | 2.8071
86 |  |  | 47171 | 47172 |  | CVOL HOURLY |  | Float (MSB 1st) | 25.0735
87 |  |  | 47173 | 47174 |  | MASS HOURLY |  | Float (MSB 1st) | 1.2476
88 |  |  | 47175 | 47176 |  | ENERGY HOURLY |  | Float (MSB 1st) | 26.5369
89 |  |  | 47177 | 47178 | STR01 FWD | UVOL HOURLY |  | Float (MSB 1st) | 2.8071
90 |  |  | 47179 | 47180 |  | CVOL HOURLY |  | Float (MSB 1st) | 25.0735
91 |  |  | 47181 | 47182 |  | MASS HOURLY |  | Float (MSB 1st) | 1.2476
92 |  |  | 47183 | 47184 |  | ENERGY HOURLY |  | Float (MSB 1st) | 26.5369
93 |  |  | 47185 | 47186 | STR02 FWD | UVOL HOURLY |  | Float (MSB 1st) | 0
94 |  |  | 47187 | 47188 |  | CVOL HOURLY |  | Float (MSB 1st) | 0
95 |  |  | 47189 | 47190 |  | MASS HOURLY |  | Float (MSB 1st) | 0
96 |  |  | 47191 | 47192 |  | ENERGY HOURLY |  | Float (MSB 1st) | 0
97 |  |  | 47193 | 47194 | STN01 FWD | UVOL HOURLY | SNAPSHOT | Float (MSB 1st) | 437.3625
98 |  |  | 47195 | 47196 |  | CVOL HOURLY |  | Float (MSB 1st) | 669.8692
99 |  |  | 47197 | 47198 |  | MASS HOURLY |  | Float (MSB 1st) | 33.3315
100 |  |  | 47199 | 47200 |  | ENERGY HOURLY |  | Float (MSB 1st) | 708.9666
101 |  |  | 47201 | 47202 | STR01 FWD | UVOL HOURLY |  | Float (MSB 1st) | 185.7776
102 |  |  | 47203 | 47204 |  | CVOL HOURLY |  | Float (MSB 1st) | 290.2494
103 |  |  | 47205 | 47206 |  | MASS HOURLY |  | Float (MSB 1st) | 14.4423
104 |  |  | 47207 | 47208 |  | ENERGY HOURLY |  | Float (MSB 1st) | 307.19
105 |  |  | 47209 | 47210 | STR02 FWD | UVOL HOURLY |  | Float (MSB 1st) | 251.5849
106 |  |  | 47211 | 47212 |  | CVOL HOURLY |  | Float (MSB 1st) | 379.6198
107 |  |  | 47213 | 47214 |  | MASS HOURLY |  | Float (MSB 1st) | 18.8892
108 |  |  | 47215 | 47216 |  | ENERGY HOURLY |  | Float (MSB 1st) | 401.7766
109 |  |  | 47217 | 47218 | STN01 FWD | UVOL HOURLY | TOTAL | Float (MSB 1st) | 1.2267
110 |  |  | 47219 | 47220 |  | CVOL HOURLY |  | Float (MSB 1st) | 10.9576
111 |  |  | 47221 | 47222 |  | MASS HOURLY |  | Float (MSB 1st) | 0.5452
112 |  |  | 47223 | 47224 |  | ENERGY HOURLY |  | Float (MSB 1st) | 11.5972
113 |  |  | 47225 | 47226 | STR01 FWD | UVOL HOURLY |  | Float (MSB 1st) | 1.2267
114 |  |  | 47227 | 47228 |  | CVOL HOURLY |  | Float (MSB 1st) | 10.9576
115 |  |  | 47229 | 47230 |  | MASS HOURLY |  | Float (MSB 1st) | 0.5452
116 |  |  | 47231 | 47232 |  | ENERGY HOURLY |  | Float (MSB 1st) | 11.5972
117 |  |  | 47233 | 47234 | STR02 FWD | UVOL HOURLY |  | Float (MSB 1st) | 0
118 |  |  | 47235 | 47236 |  | CVOL HOURLY |  | Float (MSB 1st) | 0
119 |  |  | 47237 | 47238 |  | MASS HOURLY |  | Float (MSB 1st) | 0
120 |  |  | 47239 | 47240 |  | ENERGY HOURLY |  | Float (MSB 1st) | 0
121 |  |  | 47241 | 47242 | STN01 FWD | UVOL DAILY | PREVIOUS {Daily Report -> Today Total} | Float (MSB 1st) | 6.3542
122 |  |  | 47243 | 47244 |  | CVOL DAILY |  | Float (MSB 1st) | 6.1308
123 |  |  | 47245 | 47246 |  | MASS DAILY |  | Float (MSB 1st) | 0.305
124 |  |  | 47247 | 47248 |  | ENERGY DAILY |  | Float (MSB 1st) | 6.4886
125 |  |  | 47249 | 47250 | STR01 FWD | UVOL DAILY |  | Float (MSB 1st) | 2.7384
126 |  |  | 47251 | 47252 |  | CVOL DAILY |  | Float (MSB 1st) | 2.6411
127 |  |  | 47253 | 47254 |  | MASS DAILY |  | Float (MSB 1st) | 0.1314
128 |  |  | 47255 | 47256 |  | ENERGY DAILY |  | Float (MSB 1st) | 2.7952
129 |  |  | 47257 | 47258 | STR02 FWD | UVOL DAILY |  | Float (MSB 1st) | 3.6158
130 |  |  | 47259 | 47260 |  | CVOL DAILY |  | Float (MSB 1st) | 3.4897
131 |  |  | 47261 | 47262 |  | MASS DAILY |  | Float (MSB 1st) | 0.1736
132 |  |  | 47263 | 47264 |  | ENERGY DAILY |  | Float (MSB 1st) | 3.6934
133 |  |  | 47265 | 47266 | STN01 FWD | UVOL DAILY | SNAPSHOT | Float (MSB 1st) | 6.3542
134 |  |  | 47267 | 47268 |  | CVOL DAILY |  | Float (MSB 1st) | 6.1308
135 |  |  | 47269 | 47270 |  | MASS DAILY |  | Float (MSB 1st) | 0.305
136 |  |  | 47271 | 47272 |  | ENERGY DAILY |  | Float (MSB 1st) | 6.4886
137 |  |  | 47273 | 47274 | STR01 FWD | UVOL DAILY |  | Float (MSB 1st) | 2.7384
138 |  |  | 47275 | 47276 |  | CVOL DAILY |  | Float (MSB 1st) | 2.6411
139 |  |  | 47277 | 47278 |  | MASS DAILY |  | Float (MSB 1st) | 0.1314
140 |  |  | 47279 | 47280 |  | ENERGY DAILY |  | Float (MSB 1st) | 2.7952
141 |  |  | 47281 | 47282 | STR02 FWD | UVOL DAILY |  | Float (MSB 1st) | 3.6158
142 |  |  | 47283 | 47284 |  | CVOL DAILY |  | Float (MSB 1st) | 3.4897
143 |  |  | 47285 | 47286 |  | MASS DAILY |  | Float (MSB 1st) | 0.1736
144 |  |  | 47287 | 47288 |  | ENERGY DAILY |  | Float (MSB 1st) | 3.6934
145 |  |  | 47289 | 47290 | STN01 FWD | UVOL DAILY | TOTAL {Current Report -> Today Total} | Float (MSB 1st) | 432.2357
146 |  |  | 47291 | 47292 |  | CVOL DAILY |  | Float (MSB 1st) | 674.7019
147 |  |  | 47293 | 47294 |  | MASS DAILY |  | Float (MSB 1st) | 33.572
148 |  |  | 47295 | 47296 |  | ENERGY DAILY |  | Float (MSB 1st) | 714.0814
149 |  |  | 47297 | 47298 | STR01 FWD | UVOL DAILY |  | Float (MSB 1st) | 184.2666
150 |  |  | 47299 | 47300 |  | CVOL DAILY |  | Float (MSB 1st) | 298.5718
151 |  |  | 47301 | 47302 |  | MASS DAILY |  | Float (MSB 1st) | 14.8564
152 |  |  | 47303 | 47304 |  | ENERGY DAILY |  | Float (MSB 1st) | 315.9982
153 |  |  | 47305 | 47306 | STR02 FWD | UVOL DAILY |  | Float (MSB 1st) | 247.9691
154 |  |  | 47307 | 47308 |  | CVOL DAILY |  | Float (MSB 1st) | 376.1301
155 |  |  | 47309 | 47310 |  | MASS DAILY |  | Float (MSB 1st) | 18.7156
156 |  |  | 47311 | 47312 |  | ENERGY DAILY |  | Float (MSB 1st) | 398.0832
157 |  |  | 47313 | 47314 | STN01 FWD | UVOL MONTHLY | PREVIOUS | Float (MSB 1st) | 0 | STN1_MLY_PREV_UVOL
158 |  |  | 47315 | 47316 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0 | STN1_MLY_PREV_UVOL
159 |  |  | 47317 | 47318 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
160 |  |  | 47319 | 47320 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0 | STN1_MLY_PREV_UVOL
161 |  |  | 47321 | 47322 | STR01 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 0 | STRA_MLY_PREV_UVOL
162 |  |  | 47323 | 47324 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0 | STRA_MLY_PREV_UVOL
163 |  |  | 47325 | 47326 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
164 |  |  | 47327 | 47328 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0 | STRA_MLY_PREV_UVOL
165 |  |  | 47329 | 47330 | STR02 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 0 | STRB_MLY_PREV_UVOL
166 |  |  | 47331 | 47332 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0 | STRB_MLY_PREV_UVOL
167 |  |  | 47333 | 47334 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
168 |  |  | 47335 | 47336 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0 | STRB_MLY_PREV_UVOL
169 |  |  | 47337 | 47338 |  | ENERGY MONTHLY | PREVIOUS | Float (MSB 1st) | 0
170 |  |  | 47339 | 47340 | STN01 FWD | UVOL MONTHLY | SNAPSHOT | Float (MSB 1st) | 0
171 |  |  | 47341 | 47342 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0
172 |  |  | 47343 | 47344 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
173 |  |  | 47345 | 47346 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0
174 |  |  | 47347 | 47348 | STR01 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 0
175 |  |  | 47349 | 47350 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0
176 |  |  | 47351 | 47352 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
177 |  |  | 47353 | 47354 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0
178 |  |  | 47355 | 47356 | STR02 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 0
179 |  |  | 47357 | 47358 |  | CVOL MONTHLY |  | Float (MSB 1st) | 0
180 |  |  | 47359 | 47360 |  | MASS MONTHLY |  | Float (MSB 1st) | 0
181 |  |  | 47361 | 47362 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 0
182 |  |  | 47363 | 47364 |  | ENERGY MONTHLY | SNAPSHOT | Float (MSB 1st) | 0
183 |  |  | 47365 | 47366 | STN01 FWD | UVOL MONTHLY | TOTAL | Float (MSB 1st) | 438.5899 | STN1_MLY_UVOL
184 |  |  | 47367 | 47368 |  | CVOL MONTHLY |  | Float (MSB 1st) | 680.8327 | STN1_MLY_UVOL
185 |  |  | 47369 | 47370 |  | MASS MONTHLY |  | Float (MSB 1st) | 33.877
186 |  |  | 47371 | 47372 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 720.57 | STN1_MLY_UVOL
187 |  |  | 47373 | 47374 | STR01 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 187.005 | STRA_MLY_UVOL
188 |  |  | 47375 | 47376 |  | CVOL MONTHLY |  | Float (MSB 1st) | 301.2129 | STRA_MLY_UVOL
189 |  |  | 47377 | 47378 |  | MASS MONTHLY |  | Float (MSB 1st) | 14.9878
190 |  |  | 47379 | 47380 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 318.7934 | STRA_MLY_UVOL
191 |  |  | 47381 | 47382 | STR02 FWD | UVOL MONTHLY |  | Float (MSB 1st) | 251.5849 | STRB_MLY_UVOL
192 |  |  | 47383 | 47384 |  | CVOL MONTHLY |  | Float (MSB 1st) | 379.6198 | STRB_MLY_UVOL
193 |  |  | 47385 | 47386 |  | MASS MONTHLY |  | Float (MSB 1st) | 18.8892
194 |  |  | 47387 | 47388 |  | ENERGY MONTHLY |  | Float (MSB 1st) | 401.7766 | STRB_MLY_UVOL
195 |  |  | 47389 | 47390 |  | ENERGY MONTHLY | TOTAL | Float (MSB 1st) | 401.7766
196 |  |  | 47391 | 47392 | STN01 FWD | UVOL MAINT | TOTAL | Float (MSB 1st) | 0
197 |  |  | 47393 | 47394 |  | CVOL MAINT |  | Float (MSB 1st) | 0
198 |  |  | 47395 | 47396 |  | MASS MAINT |  | Float (MSB 1st) | 0
199 |  |  | 47397 | 47398 |  | ENERGY MAINT |  | Float (MSB 1st) | 0
200 |  |  | 47399 | 47400 | STR01 FWD | UVOL MAINT |  | Float (MSB 1st) | 0
201 |  |  | 47401 | 47402 |  | CVOL MAINT |  | Float (MSB 1st) | 0
202 |  |  | 47403 | 47404 |  | MASS MAINT |  | Float (MSB 1st) | 0
203 |  |  | 47405 | 47406 |  | ENERGY MAINT |  | Float (MSB 1st) | 0
204 |  |  | 47407 | 47408 | STR02 FWD | UVOL MAINT |  | Float (MSB 1st) | 0
205 |  |  | 47409 | 47410 |  | CVOL MAINT |  | Float (MSB 1st) | 0
206 |  |  | 47411 | 47412 |  | MASS MAINT |  | Float (MSB 1st) | 0
207 |  |  | 47413 | 47414 |  | ENERGY MAINT |  | Float (MSB 1st) | 0
208 |  |  | 47415 | 47416 | STN01 | MASS FR | INUSE {FLOWRATE} | Float (MSB 1st) | 71.528
209 |  |  | 47417 | 47418 |  | UVOL FR |  | Float (MSB 1st) | 160.9346 | MCF
210 |  |  | 47419 | 47420 |  | CVOL FR |  | Float (MSB 1st) | 1437.508 | MSCF
211 |  |  | 47421 | 47422 |  | ENERGY FR |  | Float (MSB 1st) | 1521.4091 | MMBTU
212 |  |  | 47423 | 47424 | STR01 | MASS FR |  | Float (MSB 1st) | 71.528
213 |  |  | 47425 | 47426 |  | UVOL FR |  | Float (MSB 1st) | 160.9346
214 |  |  | 47427 | 47428 |  | CVOL FR |  | Float (MSB 1st) | 1437.508
215 |  |  | 47429 | 47430 |  | ENERGY FR |  | Float (MSB 1st) | 1521.4091
216 |  |  | 47431 | 47432 | STR02 | MASS FR |  | Float (MSB 1st) | 0
217 |  |  | 47433 | 47434 |  | UVOL FR |  | Float (MSB 1st) | 0
218 |  |  | 47435 | 47436 |  | CVOL FR |  | Float (MSB 1st) | 0
219 |  |  | 47437 | 47438 |  | ENERGY FR |  | Float (MSB 1st) | 0
220 |  |  | 47439 | 47440 | STN01 | CVOL FR | HILIM | Float (MSB 1st) | 720
221 |  |  | 47441 | 47442 |  |  | LOLIM | Float (MSB 1st) | -4.8
222 |  |  | 47443 | 47444 | STR01 | CVOL FR | HILIM | Float (MSB 1st) | 3700
223 |  |  | 47445 | 47446 |  |  | LOLIM | Float (MSB 1st) | -4.8
224 |  |  | 47447 | 47448 | STR02 | CVOL FR | HILIM | Float (MSB 1st) | 3700
225 |  |  | 47449 | 47450 |  |  | LOLIM | Float (MSB 1st) | -4.8
226 |  |  | 47451 | 47452 | STR01 | BASE DENS | INUSE | Float (MSB 1st) | 0.049758
227 |  |  | 47453 | 47454 |  | REAL RD (SG) |  | Float (MSB 1st) | 0.65019
228 |  |  | 47455 | 47456 |  | UPSTR COMP(Zf) |  | Float (MSB 1st) | 0.97992
229 |  |  | 47457 | 47458 |  | BASE COMP(Zb) |  | Float (MSB 1st) | 0.99746
230 |  |  | 47459 | 47460 |  | REAL CV |  | Float (MSB 1st) | 1058.3657
231 |  |  | 47461 | 47462 |  | ISENTROPIC EXP |  | Float (MSB 1st) | 1.3
232 |  |  | 47463 | 47464 |  | VISCOSITY |  | Float (MSB 1st) | 0.010268
233 |  |  | 47465 | 47466 |  | WOBBE INDEX |  | Float (MSB 1st) | 1316.3913
234 |  |  | 47467 | 47468 |  | UPSTR DENS |  | Float (MSB 1st) | 0.44445
235 |  |  | 47469 | 47470 |  | UPSTR PRESS |  | Float (MSB 1st) | 120
236 |  |  | 47471 | 47472 | STR02 | BASE DENS | INUSE | Float (MSB 1st) | 0.049758
237 |  |  | 47473 | 47474 |  | REAL RD (SG) |  | Float (MSB 1st) | 0.65019
238 |  |  | 47475 | 47476 |  | UPSTR COMP(Zf) |  | Float (MSB 1st) | 0.97992
239 |  |  | 47477 | 47478 |  | BASE COMP(Zb) |  | Float (MSB 1st) | 0.99746
240 |  |  | 47479 | 47480 |  | REAL CV |  | Float (MSB 1st) | 1058.3657
241 |  |  | 47481 | 47482 |  | ISENTROPIC EXP |  | Float (MSB 1st) | 1.3
242 |  |  | 47483 | 47484 |  | VISCOSITY |  | Float (MSB 1st) | 0.010268
243 |  |  | 47485 | 47486 |  | WOBBE INDEX |  | Float (MSB 1st) | 1316.3913
244 |  |  | 47487 | 47488 |  | UPSTR DENS |  | Float (MSB 1st) | 0.44445
245 |  |  | 47489 | 47490 |  | UPSTR PRESS |  | Float (MSB 1st) | 120
246 | CHANGES | READ / WRITE | 47491 | 47492 | STR01 | BASE TEMP(Tb) | VALUE | Float (MSB 1st) | 60
247 |  |  | 47493 | 47494 | AtmP@Base (bara/psia) |  |  | Float (MSB 1st) | 14.73
248 |  |  | 47495 | 47496 | STR01 | PIPE CAL DIAM |  | Float (MSB 1st) | 4
249 |  |  | 47497 | 47498 |  | ORIF CAL DIAM |  | Float (MSB 1st) | 2
250 |  |  | 47499 | 47500 |  | LOW FLOW CO |  | Float (MSB 1st) | 0.2
251 |  |  | 47501 | 47502 |  | PIPE CAL TEMP |  | Float (MSB 1st) | 68
252 |  |  | 47503 | 47504 |  | PIPE TEMP EXP |  | Float (MSB 1st) | 6e-06
253 |  |  | 47505 | 47506 |  | ORIF CAL TEMP |  | Float (MSB 1st) | 68
254 |  |  | 47507 | 47508 |  | ORIF EXP CONST |  | Float (MSB 1st) | 9e-06
255 |  |  | 47509 | 47510 |  | VISCOSITY (Tn) |  | Float (MSB 1st) | 59
256 |  |  | 47511 | 47512 | STR02 | BASE TEMP(Tb) |  | Float (MSB 1st) | 60
257 |  |  | 47513 | 47514 | AtmP@Base (bara/psia) |  |  | Float (MSB 1st) | 14.73
258 |  |  | 47515 | 47516 | STR02 | PIPE CAL DIAM |  | Float (MSB 1st) | 4
259 |  |  | 47517 | 47518 |  | ORIF CAL DIAM |  | Float (MSB 1st) | 2
260 |  |  | 47519 | 47520 |  | LOW FLOW CO |  | Float (MSB 1st) | 0.2
261 |  |  | 47521 | 47522 |  | PIPE CAL TEMP |  | Float (MSB 1st) | 68
262 |  |  | 47523 | 47524 |  | PIPE TEMP EXP |  | Float (MSB 1st) | 6e-06
263 |  |  | 47525 | 47526 |  | ORIF CAL TEMP |  | Float (MSB 1st) | 68
264 |  |  | 47527 | 47528 |  | ORIF EXP CONST |  | Float (MSB 1st) | 9e-06
265 |  |  | 47529 | 47530 |  | VISCOSITY (Tn) |  | Float (MSB 1st) | 59
266 |  |  | 47531 | 47532 | STN01 | CHR SETS |  | Float (MSB 1st) | 1
267 |  |  | 47533 | 47534 |  | MOLE SELECT | OUTPUT | Float (MSB 1st) | 0
268 |  |  | 47535 | 47536 |  |  | INPUT | Float (MSB 1st) | 0
269 | DISABLED | READ ONLY | 47537 | 47538 |  | CHR SLCT MOLES | NITROGEN | Float (MSB 1st) | 0.3969 | N2 | STN1_SLCT_MOL_N2 | Topic: SFCA_SEL_MOL_IKK
270 |  |  | 47539 | 47540 |  |  | CO2 | Float (MSB 1st) | 3.8979 | CO2 | STN1_SLCT_MOL_CO2
271 |  |  | 47541 | 47542 |  |  | H2S | Float (MSB 1st) | 0
272 |  |  | 47543 | 47544 |  |  | H2O | Float (MSB 1st) | 0
273 |  |  | 47545 | 47546 |  |  | METHANE | Float (MSB 1st) | 88.771 | C1 | STN1_SLCT_MOL_C1
274 |  |  | 47547 | 47548 |  |  | ETHANE | Float (MSB 1st) | 3.9573 | C2 | STN1_SLCT_MOL_C2
275 |  |  | 47549 | 47550 |  |  | PROPANE | Float (MSB 1st) | 1.9045 | C3 | STN1_SLCT_MOL_C3
276 |  |  | 47551 | 47552 |  |  | N_BUTANE | Float (MSB 1st) | 0.3891 | nC4 | STN1_SLCT_MOL_NC4
277 |  |  | 47553 | 47554 |  |  | I_BUTANE | Float (MSB 1st) | 0.3201 | iC4 | STN1_SLCT_MOL_IC4
278 |  |  | 47555 | 47556 |  |  | N_PENTANE | Float (MSB 1st) | 0.0891 | nC5 | STN1_SLCT_MOL_NC5
279 |  |  | 47557 | 47558 |  |  | I_PENTANE | Float (MSB 1st) | 0.1395 | iC5 | STN1_SLCT_MOL_IC5
280 |  |  | 47559 | 47560 |  |  | HEXANE | Float (MSB 1st) | 0.1346 | C6 | STN1_SLCT_MOL_C6
281 |  |  | 47561 | 47562 |  |  | TOTAL | Float (MSB 1st) | 100 | TOT | STN1_SLCT_MOL_TOT
282 |  |  | 47563 | 47564 |  | CHR RAW MOLES | C6 PLUS | Float (MSB 1st) | 0 | C6
283 |  |  | 47565 | 47566 |  |  | PROPANE | Float (MSB 1st) | 0 | C3
284 |  |  | 47567 | 47568 |  |  | iBUTANE | Float (MSB 1st) | 0 | iC4
285 |  |  | 47569 | 47570 |  |  | nBUTANE | Float (MSB 1st) | 0 | nC4
286 |  |  | 47571 | 47572 |  |  | nPENTANE | Float (MSB 1st) | 0 | nC5
287 |  |  | 47573 | 47574 |  |  | iPENTANE | Float (MSB 1st) | 0 | iC5
288 |  |  | 47575 | 47576 |  |  | NITROGEN | Float (MSB 1st) | 0 | N2
289 |  |  | 47577 | 47578 |  |  | METHANE | Float (MSB 1st) | 0 | C1
290 |  |  | 47579 | 47580 |  |  | CO2 | Float (MSB 1st) | 0 | CO2
291 |  |  | 47581 | 47582 |  |  | ETHANE | Float (MSB 1st) | 0 | C2
292 |  |  | 47583 | 47584 |  | CHR RAW MISC | BTU DRY | Float (MSB 1st) | 0
293 |  |  | 47585 | 47586 |  |  | BTU SAT | Float (MSB 1st) | 0
294 |  |  | 47587 | 47588 |  |  | SG | Float (MSB 1st) | 0
295 |  |  | 47589 | 47590 |  |  | COMPRESSIBILITY | Float (MSB 1st) | 0
296 |  |  | 47591 | 47592 |  |  | WOBBE INDEX | Float (MSB 1st) | 0
297 |  |  | 47593 | 47594 |  |  | TOTAL UNNORM | Float (MSB 1st) | 0
298 |  |  | 47595 | 47596 |  |  | MOLAR MAS | Float (MSB 1st) | 0
299 | CHANGES | READ / WRITE | 47597 | 47598 |  | KEYPAD MOLES | NITROGEN | Float (MSB 1st) | 0.3969
300 |  |  | 47599 | 47600 |  |  | CO2 | Float (MSB 1st) | 3.8979
301 |  |  | 47601 | 47602 |  |  | H2S | Float (MSB 1st) | 0
302 |  |  | 47603 | 47604 |  |  | H2O | Float (MSB 1st) | 0
303 |  |  | 47605 | 47606 |  |  | METHANE | Float (MSB 1st) | 88.771
304 |  |  | 47607 | 47608 |  |  | ETHANE | Float (MSB 1st) | 3.9573
305 |  |  | 47609 | 47610 |  |  | PROPANE | Float (MSB 1st) | 1.9045
306 |  |  | 47611 | 47612 |  |  | N_BUTANE | Float (MSB 1st) | 0.3891
307 |  |  | 47613 | 47614 |  |  | I_BUTANE | Float (MSB 1st) | 0.3201
308 |  |  | 47615 | 47616 |  |  | N_PENTANE | Float (MSB 1st) | 0.0891
309 |  |  | 47617 | 47618 |  |  | I_PENTANE | Float (MSB 1st) | 0.1395
310 |  |  | 47619 | 47620 |  |  | HEXANE | Float (MSB 1st) | 0.1346
311 |  |  | 47621 | 47622 |  |  | TOTAL | Float (MSB 1st) | 100
312 |  |  | 47623 | 47624 |  | CHR K_ACCEPT | VALUE | Float (MSB 1st) | 0
313 | DISABLED | READ ONLY | 47625 | 47626 |  | GC INT 9026 | RUN TIME | Float (MSB 1st) | 0
314 |  |  | 47627 | 47628 |  |  | CURRENT STREAM | Float (MSB 1st) | 0
315 |  |  | 47629 | 47630 |  |  | GC MODE | Float (MSB 1st) | 0
316 |  |  | 47631 | 47632 |  |  | CALIBRATING | Float (MSB 1st) | 0
317 |  |  | 47633 | 47634 |  |  | ACTIVE ALM | Float (MSB 1st) | 0
318 |  |  | 47635 | 47636 |  |  | UNACK ALARM | Float (MSB 1st) | 0
319 | CHANGES | READ / WRITE | 47637 | 47638 | STR01 | MAINT MODE | VALUE | Float (MSB 1st) | 0
320 | DISABLED | READ ONLY | 47639 | 47640 |  | STATUS | VALUE | Float (MSB 1st) | 1
321 | CHANGES | READ / WRITE | 47641 | 47642 | STR02 | MAINT MODE | VALUE | Float (MSB 1st) | 0
322 | DISABLED | READ ONLY | 47643 | 47644 |  | STATUS | VALUE | Float (MSB 1st) | 2
323 |  |  | 47645 | 47646 | STR01 | PREV PRESS | HOURLY IK {Hourly Averaged Flowrate} | Float (MSB 1st) | 120 | PSIG
324 |  |  | 47647 | 47648 |  | PREV TEMP |  | Float (MSB 1st) | 82 | deg.F
325 |  |  | 47649 | 47650 |  | PREV DPT |  | Float (MSB 1st) | 25 | inH2O
326 |  |  | 47651 | 47652 |  | PREV GHV |  | Float (MSB 1st) | 1058.3657
327 |  |  | 47653 | 47654 |  | PREV UVOL FR |  | Float (MSB 1st) | 160.9346
328 |  |  | 47655 | 47656 |  | PREV CVOL FR |  | Float (MSB 1st) | 1437.508
329 |  |  | 47657 | 47658 |  | PREV ENERGY FR |  | Float (MSB 1st) | 1521.4091
330 |  |  | 47659 | 47660 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 1316.3913 | BTU/SCF
331 |  |  | 47661 | 47662 |  | PREV BASE DENS |  | Float (MSB 1st) | 0.049758
332 |  |  | 47663 | 47664 |  | PREV LINE DENS |  | Float (MSB 1st) | 0.44445
333 |  |  | 47665 | 47666 |  | PREV BASE COMP |  | Float (MSB 1st) | 0.99746
334 |  |  | 47667 | 47668 |  | PREV LINE COMP |  | Float (MSB 1st) | 0.97992
335 |  |  | 47669 | 47670 |  | PREV SG |  | Float (MSB 1st) | 0.65019
336 |  |  | 47671 | 47672 |  | PREV PRESS | DAILY IK | Float (MSB 1st) | 0
337 |  |  | 47673 | 47674 |  | PREV TEMP |  | Float (MSB 1st) | 0
338 |  |  | 47675 | 47676 |  | PREV DPT |  | Float (MSB 1st) | 0
339 |  |  | 47677 | 47678 |  | PREV GHV |  | Float (MSB 1st) | 0
340 |  |  | 47679 | 47680 |  | PREV UVOL FR |  | Float (MSB 1st) | 0
341 |  |  | 47681 | 47682 |  | PREV CVOL FR |  | Float (MSB 1st) | 0
342 |  |  | 47683 | 47684 |  | PREV ENERGY FR |  | Float (MSB 1st) | 0
343 |  |  | 47685 | 47686 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 0
344 |  |  | 47687 | 47688 |  | PREV BASE DENS |  | Float (MSB 1st) | 0
345 |  |  | 47689 | 47690 |  | PREV LINE DENS |  | Float (MSB 1st) | 0
346 |  |  | 47691 | 47692 |  | PREV BASE COMP |  | Float (MSB 1st) | 0
347 |  |  | 47693 | 47694 |  | PREV LINE COMP |  | Float (MSB 1st) | 0
348 |  |  | 47695 | 47696 |  | PREV SG |  | Float (MSB 1st) | 0
349 |  |  | 47697 | 47698 |  | PREV PRESS | MONTHLY IK | Float (MSB 1st) | 0
350 |  |  | 47699 | 47700 |  | PREV TEMP |  | Float (MSB 1st) | 0
351 |  |  | 47701 | 47702 |  | PREV DPT |  | Float (MSB 1st) | 0
352 |  |  | 47703 | 47704 |  | PREV GHV |  | Float (MSB 1st) | 0
353 |  |  | 47705 | 47706 |  | PREV UVOL FR |  | Float (MSB 1st) | 0
354 |  |  | 47707 | 47708 |  | PREV CVOL FR |  | Float (MSB 1st) | 0
355 |  |  | 47709 | 47710 |  | PREV ENERGY FR |  | Float (MSB 1st) | 0
356 |  |  | 47711 | 47712 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 0
357 |  |  | 47713 | 47714 |  | PREV BASE DENS |  | Float (MSB 1st) | 0
358 |  |  | 47715 | 47716 |  | PREV LINE DENS |  | Float (MSB 1st) | 0
359 |  |  | 47717 | 47718 |  | PREV BASE COMP |  | Float (MSB 1st) | 0
360 |  |  | 47719 | 47720 |  | PREV LINE COMP |  | Float (MSB 1st) | 0
361 |  |  | 47721 | 47722 |  | PREV SG |  | Float (MSB 1st) | 0
362 |  |  | 47723 | 47724 | STR02 | PREV PRESS | HOURLY IK {Hourly Averaged Flowrate} | Float (MSB 1st) | 0
363 |  |  | 47725 | 47726 |  | PREV TEMP |  | Float (MSB 1st) | 0
364 |  |  | 47727 | 47728 |  | PREV DPT |  | Float (MSB 1st) | 0
365 |  |  | 47729 | 47730 |  | PREV GHV |  | Float (MSB 1st) | 0
366 |  |  | 47731 | 47732 |  | PREV UVOL FR |  | Float (MSB 1st) | 0
367 |  |  | 47733 | 47734 |  | PREV CVOL FR |  | Float (MSB 1st) | 0
368 |  |  | 47735 | 47736 |  | PREV ENERGY FR |  | Float (MSB 1st) | 0
369 |  |  | 47737 | 47738 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 0
370 |  |  | 47739 | 47740 |  | PREV BASE DENS |  | Float (MSB 1st) | 0
371 |  |  | 47741 | 47742 |  | PREV LINE DENS |  | Float (MSB 1st) | 0
372 |  |  | 47743 | 47744 |  | PREV BASE COMP |  | Float (MSB 1st) | 0
373 |  |  | 47745 | 47746 |  | PREV LINE COMP |  | Float (MSB 1st) | 0
374 |  |  | 47747 | 47748 |  | PREV SG |  | Float (MSB 1st) | 0
375 |  |  | 47749 | 47750 |  | PREV PRESS | DAILY IK | Float (MSB 1st) | 0
376 |  |  | 47751 | 47752 |  | PREV TEMP |  | Float (MSB 1st) | 0
377 |  |  | 47753 | 47754 |  | PREV DPT |  | Float (MSB 1st) | 0
378 |  |  | 47755 | 47756 |  | PREV GHV |  | Float (MSB 1st) | 0
379 |  |  | 47757 | 47758 |  | PREV UVOL FR |  | Float (MSB 1st) | 0
380 |  |  | 47759 | 47760 |  | PREV CVOL FR |  | Float (MSB 1st) | 0
381 |  |  | 47761 | 47762 |  | PREV ENERGY FR |  | Float (MSB 1st) | 0
382 |  |  | 47763 | 47764 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 0
383 |  |  | 47765 | 47766 |  | PREV BASE DENS |  | Float (MSB 1st) | 0
384 |  |  | 47767 | 47768 |  | PREV LINE DENS |  | Float (MSB 1st) | 0
385 |  |  | 47769 | 47770 |  | PREV BASE COMP |  | Float (MSB 1st) | 0
386 |  |  | 47771 | 47772 |  | PREV LINE COMP |  | Float (MSB 1st) | 0
387 |  |  | 47773 | 47774 |  | PREV SG |  | Float (MSB 1st) | 0
388 |  |  | 47775 | 47776 |  | PREV PRESS | MONTHLY IK | Float (MSB 1st) | 0
389 |  |  | 47777 | 47778 |  | PREV TEMP |  | Float (MSB 1st) | 0
390 |  |  | 47779 | 47780 |  | PREV DPT |  | Float (MSB 1st) | 0
391 |  |  | 47781 | 47782 |  | PREV GHV |  | Float (MSB 1st) | 0
392 |  |  | 47783 | 47784 |  | PREV UVOL FR |  | Float (MSB 1st) | 0
393 |  |  | 47785 | 47786 |  | PREV CVOL FR |  | Float (MSB 1st) | 0
394 |  |  | 47787 | 47788 |  | PREV ENERGY FR |  | Float (MSB 1st) | 0
395 |  |  | 47789 | 47790 |  | PREV WOBBEINDEX |  | Float (MSB 1st) | 0
396 |  |  | 47791 | 47792 |  | PREV BASE DENS |  | Float (MSB 1st) | 0
397 |  |  | 47793 | 47794 |  | PREV LINE DENS |  | Float (MSB 1st) | 0
398 |  |  | 47795 | 47796 |  | PREV BASE COMP |  | Float (MSB 1st) | 0
399 |  |  | 47797 | 47798 |  | PREV LINE COMP |  | Float (MSB 1st) | 0
400 |  |  | 47799 | 47800 |  | PREV SG |  | Float (MSB 1st) | 0
401 |  |  | 47801 | 47802 | STR01 | GCFWA HOURLY | NITROGEN | Float (MSB 1st) | 0.3969 | N2
402 |  |  | 47803 | 47804 |  |  | CO2 | Float (MSB 1st) | 3.8979 | CO2
403 |  |  | 47805 | 47806 |  |  | METHANE | Float (MSB 1st) | 88.771 | C1
404 |  |  | 47807 | 47808 |  |  | ETHANE | Float (MSB 1st) | 3.9573 | C2
405 |  |  | 47809 | 47810 |  |  | PROPANE | Float (MSB 1st) | 1.9045 | C3
406 |  |  | 47811 | 47812 |  |  | N_BUTANE | Float (MSB 1st) | 0.3891 | nC4
407 |  |  | 47813 | 47814 |  |  | I_BUTANE | Float (MSB 1st) | 0.3201 | iC4
408 |  |  | 47815 | 47816 |  |  | N_PENTANE | Float (MSB 1st) | 0.0891 | nC5
409 |  |  | 47817 | 47818 |  |  | I_PENTANE | Float (MSB 1st) | 0.1395 | iC5
410 |  |  | 47819 | 47820 |  |  | HEXANE | Float (MSB 1st) | 0.1346 | C6
411 |  |  | 47821 | 47822 |  |  | TOTAL | Float (MSB 1st) | 100
412 |  |  | 47823 | 47824 | STR02 | GCFWA DAILY | NITROGEN | Float (MSB 1st) | 0 | N2
413 |  |  | 47825 | 47826 |  |  | CO2 | Float (MSB 1st) | 0 | CO2
414 |  |  | 47827 | 47828 |  |  | METHANE | Float (MSB 1st) | 0 | C1
415 |  |  | 47829 | 47830 |  |  | ETHANE | Float (MSB 1st) | 0 | C2
416 |  |  | 47831 | 47832 |  |  | PROPANE | Float (MSB 1st) | 0 | C3
417 |  |  | 47833 | 47834 |  |  | N_BUTANE | Float (MSB 1st) | 0 | nC4
418 |  |  | 47835 | 47836 |  |  | I_BUTANE | Float (MSB 1st) | 0 | iC4
419 |  |  | 47837 | 47838 |  |  | N_PENTANE | Float (MSB 1st) | 0 | nC5
420 |  |  | 47839 | 47840 |  |  | I_PENTANE | Float (MSB 1st) | 0 | iC5
421 |  |  | 47841 | 47842 |  |  | HEXANE | Float (MSB 1st) | 0 | C6
422 |  |  | 47843 | 47844 |  |  | TOTAL | Float (MSB 1st) | 0
423 |  |  | 47845 | 47846 |  | GCFWA MONTHLY | NITROGEN | Float (MSB 1st) | 0 | N2
424 |  |  | 47847 | 47848 |  |  | CO2 | Float (MSB 1st) | 0 | CO2
425 |  |  | 47849 | 47850 |  |  | METHANE | Float (MSB 1st) | 0 | C1
426 |  |  | 47851 | 47852 |  |  | ETHANE | Float (MSB 1st) | 0 | C2
427 |  |  | 47853 | 47854 |  |  | PROPANE | Float (MSB 1st) | 0 | C3
428 |  |  | 47855 | 47856 |  |  | N_BUTANE | Float (MSB 1st) | 0 | nC4
429 |  |  | 47857 | 47858 |  |  | I_BUTANE | Float (MSB 1st) | 0 | iC4
430 |  |  | 47859 | 47860 |  |  | N_PENTANE | Float (MSB 1st) | 0 | nC5
431 |  |  | 47861 | 47862 |  |  | I_PENTANE | Float (MSB 1st) | 0 | iC5
432 |  |  | 47863 | 47864 |  |  | HEXANE | Float (MSB 1st) | 0 | C6
433 |  |  | 47865 | 47866 |  |  | TOTAL | Float (MSB 1st) | 0
434 |  |  | 47867 | 47868 | TIME AND DATE | CUR. YEAR |  | Float (MSB 1st) | 2025
435 |  |  | 47869 | 47870 |  | CUR. MONTH |  | Float (MSB 1st) | 7
436 |  |  | 47871 | 47872 |  | CUR. DAY |  | Float (MSB 1st) | 21
437 |  |  | 47873 | 47874 |  | CUR. HOUR |  | Float (MSB 1st) | 21
438 |  |  | 47875 | 47876 |  | CUR. MINUTE |  | Float (MSB 1st) | 10
439 |  |  | 47877 | 47878 |  | CUR. SECOND |  | Float (MSB 1st) | 59
440 | CHANGES | READ / WRITE | 47879 | 47880 |  | DLOAD YEAR |  | Float (MSB 1st) | 2025 |  | DLOAD_YEAR_A | Topic: FCA_DATETIME_IKK
441 |  |  | 47881 | 47882 |  | DLOAD MONTH |  | Float (MSB 1st) | 7 |  | DLOAD_MONTH_A
442 |  |  | 47883 | 47884 |  | DLOAD DAY |  | Float (MSB 1st) | 21 |  | DLOAD_DAY_A
443 |  |  | 47885 | 47886 |  | DLOAD HOUR |  | Float (MSB 1st) | 20 |  | DLOAD_HOUR_A
444 |  |  | 47887 | 47888 |  | DLOAD MINUTE |  | Float (MSB 1st) | 55 |  | DLOAD_MINUTE_A
445 |  |  | 47889 | 47890 |  | DLOAD SECOND |  | Float (MSB 1st) | 19 |  | DLOAD_SECOND_A
446 |  |  | 47891 | 47892 | DLOAD TIME ACCEPT | VALUE |  | Float (MSB 1st) | 0 |  | DLOAD_TIMEACC_A
447 |  |  | 47893 | 47894 | SYS PEER STAT | OUTPUT |  | Float (MSB 1st) | 0
448 | DISABLED | READ ONLY | 47895 | 47896 |  | INPUT |  | Float (MSB 1st) | 3
449 |  |  | 47897 | 47898 | STN01 GC INT 9026 | RUN TIME |  | Float (MSB 1st) | 0
450 |  |  | 47899 | 47900 |  | CURRENT STREAM |  | Float (MSB 1st) | 0
451 |  |  | 47901 | 47902 |  | GC MODE |  | Float (MSB 1st) | 0
452 |  |  | 47903 | 47904 |  | CALIBRATING |  | Float (MSB 1st) | 0
453 |  |  | 47905 | 47906 |  | ACTIVE ALM |  | Float (MSB 1st) | 0
454 |  |  | 47907 | 47908 |  | UNACK ALARM |  | Float (MSB 1st) | 0
455 | ALL | READ / WRITE | 47909 | 47910 | SDV VLV | OUTPUT |  | Float (MSB 1st) | 0
456 | DISABLED | READ ONLY | 47911 | 47912 |  | INPUT |  | Float (MSB 1st) | 0
457 | CHANGES | READ / WRITE | 47913 | 47914 | ESD BUTTON | INPUT |  | Float (MSB 1st) | 1
458 | CHANGES | READ / WRITE | 47915 | 47916 | PT-12501-04 | HIHILIM |  | Float (MSB 1st) | 450
459 |  |  | 47917 | 47918 |  | HILIM |  | Float (MSB 1st) | 400
460 |  |  | 47919 | 47920 |  | LOLIM |  | Float (MSB 1st) | 60
461 |  |  | 47921 | 47922 |  | LOLOLIM |  | Float (MSB 1st) | 30
462 |  |  | 47923 | 47924 | PT-12501-05 | HIHILIM |  | Float (MSB 1st) | 150
463 |  |  | 47925 | 47926 |  | HILIM |  | Float (MSB 1st) | 120
464 |  |  | 47927 | 47928 |  | LOLIM |  | Float (MSB 1st) | 50
465 |  |  | 47929 | 47930 |  | LOLOLIM |  | Float (MSB 1st) | 25
466 | DISABLED | READ ONLY | 47931 | 47932 | STN01 CVOL FR | RAW |  | Float (MSB 1st) | 1437.508
467 | CHANGES | READ / WRITE | 47933 | 47934 |  | LOSCALE |  | Float (MSB 1st) | 0
468 |  |  | 47935 | 47936 |  | HISCALE |  | Float (MSB 1st) | 5000
469 | DISABLED | READ ONLY | 47937 | 47938 | STR01 CVOL FR | RAW |  | Float (MSB 1st) | 1437.508
470 | CHANGES | READ / WRITE | 47939 | 47940 |  | LOSCALE |  | Float (MSB 1st) | 0
471 |  |  | 47941 | 47942 |  | HISCALE |  | Float (MSB 1st) | 5000
472 | DISABLED | READ ONLY | 47943 | 47944 | STR02 CVOL FR | RAW |  | Float (MSB 1st) | 0
473 | CHANGES | READ / WRITE | 47945 | 47946 |  | LOSCALE |  | Float (MSB 1st) | 0
474 |  |  | 47947 | 47948 |  | HISCALE |  | Float (MSB 1st) | 5000
475 |  |  | 47949 | 47950 | ESD BUTTON | OUTPUT |  | Float (MSB 1st) | 1
|  |  | 47951 | 47952 | ESD BUTTON INHIBIT | OUTPUT |  | Float (MSB 1st) | 0
|  |  | 47953 | 47954 | PT-12501-04 INHIBIT | OUTPUT |  | Float (MSB 1st) | 0
|  |  | 47955 | 47956 | PT-12501-05 INHIBIT | OUTPUT |  | Float (MSB 1st) | 0

## Hourly Rep
Hourly Report
Input :
1 | Flow Computer ID
2 | Date
3 | Time
Command :
1 | Print
| METER ID |  | MS-12501-01 | MS-12501-01 | Station Total
FISCAL HOURLY (Previous)
| HOURLY GROSS | MCF | 47178 | 47186 | 47170
| HOURLY NET | MSCF | 47180 | 47188 | 47172
| HOURLY ENERGY | MMBTU | 47184 | 47192 | 47176
FISCAL TOTALIZER (Snapshot)
| CUM. GROSS | MCF | 47202 | 47210 | 47194
| CUM. NET | MSCF | 47204 | 47212 | 47196
| CUM. ENERGY | MMBTU | 47208 | 47216 | 47200
HOURLY AVERAGED FLOWRATE
| HOURLY GROSS | MCFD | 47654 | 47732
| HOURLY NET | MSCFD | 47656 | 47734
| HOURLY ENERGY | MMBTUD | 47658 | 47736
MAINTENANCE TOTALIZER
| CUM. GROSS | MCF | 47400 | 47408
| CUM. NET | MSCF | 47402 | 47410
| CUM. ENERGY | MMBTU | 47406 | 47414
FLOW WEIGHTED HOURLY AVERAGED DATA
| METER PRESSURE | psig | 47646 | 47724
| METER TEMPERATURE | deg.F | 47648 | 47726
| METER DIFF. PRESS. | inH2O | 47650 | 47728
| BASE PRESSURE | psia | 47494 | 47514
| BASE TEMPERATURE | deg.F | 47492 | 47512
| BASE DENSITY | lbs/CF | 47662 | 47740
| METER DENSITY | lbs/CF | 47664 | 47742
| HEATING VALUE | BTU/SCF | 47652 | 47730
| WOBBE INDEX | BTU/SCF | 47660 | 47738
| S.G. | - | 47670 | 47748
HOURLY AVERAGED GAS COMPOSITIONS (MOL%)
| METHANE | mol% | 47806
| ETHANE | mol% | 47808
| PROPANE | mol% | 47810
| i-BUTANE | mol% | 47814
| n-BUTANE | mol% | 47812
| i-PENTANE | mol% | 47818
| n-PENTANE | mol% | 47816
| HEXANE | mol% | 47820
| CO2 | mol% | 47804
| NITROGEN | mol% | 47802
| TOTAL | mol% | 47822

## Daily Rep
Daily Report
Input :
1 | Flow Computer ID
2 | Date
3 | Time
Command :
1 | Print
| METER ID |  | MS-12501-01 | MS-12501-01 | Station Total
FISCAL HOURLY (Previous)
| HOURLY GROSS | MCF | 47250 | 47258 | 47242
| HOURLY NET | MSCF | 47252 | 47260 | 47244
| HOURLY ENERGY | MMBTU | 47256 | 47264 | 47248
FISCAL TOTALIZER (Snapshot)
| CUM. GROSS | MCF | 47274 | 47282 | 47266
| CUM. NET | MSCF | 47276 | 47284 | 47268
| CUM. ENERGY | MMBTU | 47280 | 47287 | 47272
HOURLY AVERAGED FLOWRATE
| HOURLY GROSS | MCFD | 47680 | 47758
| HOURLY NET | MSCFD | 47682 | 47760
| HOURLY ENERGY | MMBTUD | 47684 | 47762
MAINTENANCE TOTALIZER
| CUM. GROSS | MCF | 47400 | 47408
| CUM. NET | MSCF | 47402 | 47410
| CUM. ENERGY | MMBTU | 47406 | 47414
FLOW WEIGHTED HOURLY AVERAGED DATA
| METER PRESSURE | psig | 47672 | 47750
| METER TEMPERATURE | deg.F | 47674 | 47752
| METER DIFF. PRESS. | inH2O | 47676 | 47754
| BASE PRESSURE | psia | 47494 | 47514
| BASE TEMPERATURE | deg.F | 47492 | 47512
| BASE DENSITY | lbs/CF | 47688 | 47766
| METER DENSITY | lbs/CF | 47690 | 47768
| HEATING VALUE | BTU/SCF | 47678 | 47756
| WOBBE INDEX | BTU/SCF | 47686 | 47764
| S.G. | - | 47696 | 47774
HOURLY AVERAGED GAS COMPOSITIONS (MOL%)
| METHANE | mol% | 47828
| ETHANE | mol% | 47830
| PROPANE | mol% | 47832
| i-BUTANE | mol% | 47836
| n-BUTANE | mol% | 47834
| i-PENTANE | mol% | 47840
| n-PENTANE | mol% | 47838
| HEXANE | mol% | 47842
| CO2 | mol% | 47826
| NITROGEN | mol% | 47824
| TOTAL | mol% | 47844

## 20250721_ModbusMap_S600
Modbus map
SLAVE LINK 1 : TCP/IP socket 4
===========================================
PROTOCOL
========
MODBUS TCP SLAVE
SLAVE NUMBER 1
===============
REGISTER DATA MAP
=================
Block number 1
================
EVENTING MODE : CHANGES
SECURITY LEVEL : READ / WRITE
07001 1B59H PT-12501-01 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07003 1B5BH PT-12501-01 INUSE Float (MSB 1st) 120.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07005 1B5DH PT-12501-01 KEYPAD Float (MSB 1st) 120.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07007 1B5FH PT-12501-01 MEASURED Float (MSB 1st) -124.986168
07009 1B61H PT-12501-01 CURRENT Float (MSB 1st) 0.000443
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07011 1B63H PT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07013 1B65H PT-12501-01 HISCALE Float (MSB 1st) 500.000000
07015 1B67H PT-12501-01 HILIM Float (MSB 1st) 200.000000
07017 1B69H PT-12501-01 LOLIM Float (MSB 1st) 60.000000
07019 1B6BH DPT-12501-01 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07021 1B6DH DPT-12501-01 INUSE Float (MSB 1st) 0.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07023 1B6FH DPT-12501-01 KEYPAD Float (MSB 1st) 0.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07025 1B71H DPT-12501-01 MEASURED Float (MSB 1st) -49.993749
07027 1B73H DPT-12501-01 CURRENT Float (MSB 1st) 0.000500
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07029 1B75H DPT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07031 1B77H DPT-12501-01 HISCALE Float (MSB 1st) 200.000000
07033 1B79H DPT-12501-01 HILIM Float (MSB 1st) 200.000000
07035 1B7BH DPT-12501-01 LOLIM Float (MSB 1st) -2.000000
07037 1B7DH TT-12501-01 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07039 1B7FH TT-12501-01 INUSE Float (MSB 1st) 82.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07041 1B81H TT-12501-01 KEYPAD Float (MSB 1st) 82.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07043 1B83H TT-12501-01 MEASURED Float (MSB 1st) -37.495089
07045 1B85H TT-12501-01 CURRENT Float (MSB 1st) 0.000524
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07047 1B87H TT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07049 1B89H TT-12501-01 HISCALE Float (MSB 1st) 150.000000
07051 1B8BH TT-12501-01 HILIM Float (MSB 1st) 86.000000
07053 1B8DH TT-12501-01 LOLIM Float (MSB 1st) 75.000000
07055 1B8FH PT-12501-04 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07057 1B91H PT-12501-04 INUSE Float (MSB 1st) 300.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07059 1B93H PT-12501-04 KEYPAD Float (MSB 1st) 300.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07061 1B95H PT-12501-04 MEASURED Float (MSB 1st) -124.983837
07063 1B97H PT-12501-04 CURRENT Float (MSB 1st) 0.000517
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07065 1B99H PT-12501-04 LOSCALE Float (MSB 1st) 0.000000
07067 1B9BH PT-12501-04 HISCALE Float (MSB 1st) 500.000000
07069 1B9DH PT-12501-04 HILIM Float (MSB 1st) 400.000000
07071 1B9FH PT-12501-04 LOLIM Float (MSB 1st) 60.000000
07073 1BA1H PT-12501-05 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07075 1BA3H PT-12501-05 INUSE Float (MSB 1st) 200.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07077 1BA5H PT-12501-05 KEYPAD Float (MSB 1st) 200.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07079 1BA7H PT-12501-05 MEASURED Float (MSB 1st) -124.982040
07081 1BA9H PT-12501-05 CURRENT Float (MSB 1st) 0.000575
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07083 1BABH PT-12501-05 LOSCALE Float (MSB 1st) 0.000000
07085 1BADH PT-12501-05 HISCALE Float (MSB 1st) 500.000000
07087 1BAFH PT-12501-05 HILIM Float (MSB 1st) 120.000000
07089 1BB1H PT-12501-05 LOLIM Float (MSB 1st) 50.000000
07091 1BB3H PT-12501-02 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07093 1BB5H PT-12501-02 INUSE Float (MSB 1st) 120.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07095 1BB7H PT-12501-02 KEYPAD Float (MSB 1st) 120.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07097 1BB9H PT-12501-02 MEASURED Float (MSB 1st) -124.982501
07099 1BBBH PT-12501-02 CURRENT Float (MSB 1st) 0.000560
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07101 1BBDH PT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07103 1BBFH PT-12501-02 HISCALE Float (MSB 1st) 500.000000
07105 1BC1H PT-12501-02 HILIM Float (MSB 1st) 200.000000
07107 1BC3H PT-12501-02 LOLIM Float (MSB 1st) 60.000000
07109 1BC5H DPT-12501-02 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07111 1BC7H DPT-12501-02 INUSE Float (MSB 1st) 0.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07113 1BC9H DPT-12501-02 KEYPAD Float (MSB 1st) 0.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07115 1BCBH DPT-12501-02 MEASURED Float (MSB 1st) -49.993800
07117 1BCDH DPT-12501-02 CURRENT Float (MSB 1st) 0.000496
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07119 1BCFH DPT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07121 1BD1H DPT-12501-02 HISCALE Float (MSB 1st) 200.000000
07123 1BD3H DPT-12501-02 HILIM Float (MSB 1st) 200.000000
07125 1BD5H DPT-12501-02 LOLIM Float (MSB 1st) -2.000000
07127 1BD7H TT-12501-02 MODE Float (MSB 1st) 4
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07129 1BD9H TT-12501-02 INUSE Float (MSB 1st) 82.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07131 1BDBH TT-12501-02 KEYPAD Float (MSB 1st) 82.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07133 1BDDH TT-12501-02 MEASURED Float (MSB 1st) -37.493839
07135 1BDFH TT-12501-02 CURRENT Float (MSB 1st) 0.000657
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07137 1BE1H TT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07139 1BE3H TT-12501-02 HISCALE Float (MSB 1st) 150.000000
07141 1BE5H TT-12501-02 HILIM Float (MSB 1st) 86.000000
07143 1BE7H TT-12501-02 LOLIM Float (MSB 1st) 75.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07145 1BE9H STN01 FWD UVOL TOTAL Float (MSB 1st) 438.589200
07147 1BEBH STN01 FWD CVOL TOTAL Float (MSB 1st) 680.826800
07149 1BEDH STN01 FWD MASS TOTAL Float (MSB 1st) 33.876700
07151 1BEFH STN01 FWD ENERGY TOTAL Float (MSB 1st) 720.563800
07153 1BF1H STR01 FWD UVOL TOTAL Float (MSB 1st) 187.004300
07155 1BF3H STR01 FWD CVOL TOTAL Float (MSB 1st) 301.207000
07157 1BF5H STR01 FWD MASS TOTAL Float (MSB 1st) 14.987500
07159 1BF7H STR01 FWD ENERGY TOTAL Float (MSB 1st) 318.787200
07161 1BF9H STR02 FWD UVOL TOTAL Float (MSB 1st) 251.584900
07163 1BFBH STR02 FWD CVOL TOTAL Float (MSB 1st) 379.619800
07165 1BFDH STR02 FWD MASS TOTAL Float (MSB 1st) 18.889200
07167 1BFFH STR02 FWD ENERGY TOTAL Float (MSB 1st) 401.776600
07169 1C01H STN01 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 2.807100
07171 1C03H STN01 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 25.073500
07173 1C05H STN01 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 1.247600
07175 1C07H STN01 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 26.536900
07177 1C09H STR01 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 2.807100
07179 1C0BH STR01 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 25.073500
07181 1C0DH STR01 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 1.247600
07183 1C0FH STR01 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 26.536900
07185 1C11H STR02 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 0.000000
07187 1C13H STR02 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 0.000000
07189 1C15H STR02 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 0.000000
07191 1C17H STR02 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 0.000000
07193 1C19H STN01 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 437.362500
07195 1C1BH STN01 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 669.869200
07197 1C1DH STN01 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 33.331500
07199 1C1FH STN01 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 708.966600
07201 1C21H STR01 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 185.777600
07203 1C23H STR01 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 290.249400
07205 1C25H STR01 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 14.442300
07207 1C27H STR01 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 307.190000
07209 1C29H STR02 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 251.584900
07211 1C2BH STR02 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 379.619800
07213 1C2DH STR02 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 18.889200
07215 1C2FH STR02 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 401.776600
07217 1C31H STN01 FWD UVOL HOURLY TOTAL Float (MSB 1st) 1.226700
07219 1C33H STN01 FWD CVOL HOURLY TOTAL Float (MSB 1st) 10.957600
07221 1C35H STN01 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.545200
07223 1C37H STN01 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 11.597200
07225 1C39H STR01 FWD UVOL HOURLY TOTAL Float (MSB 1st) 1.226700
07227 1C3BH STR01 FWD CVOL HOURLY TOTAL Float (MSB 1st) 10.957600
07229 1C3DH STR01 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.545200
07231 1C3FH STR01 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 11.597200
07233 1C41H STR02 FWD UVOL HOURLY TOTAL Float (MSB 1st) 0.000000
07235 1C43H STR02 FWD CVOL HOURLY TOTAL Float (MSB 1st) 0.000000
07237 1C45H STR02 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.000000
07239 1C47H STR02 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 0.000000
07241 1C49H STN01 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 6.354200
07243 1C4BH STN01 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 6.130800
07245 1C4DH STN01 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.305000
07247 1C4FH STN01 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 6.488600
07249 1C51H STR01 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 2.738400
07251 1C53H STR01 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 2.641100
07253 1C55H STR01 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.131400
07255 1C57H STR01 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 2.795200
07257 1C59H STR02 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 3.615800
07259 1C5BH STR02 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 3.489700
07261 1C5DH STR02 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.173600
07263 1C5FH STR02 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 3.693400
07265 1C61H STN01 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 6.354200
07267 1C63H STN01 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 6.130800
07269 1C65H STN01 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.305000
07271 1C67H STN01 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 6.488600
07273 1C69H STR01 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 2.738400
07275 1C6BH STR01 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 2.641100
07277 1C6DH STR01 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.131400
07279 1C6FH STR01 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 2.795200
07281 1C71H STR02 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 3.615800
07283 1C73H STR02 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 3.489700
07285 1C75H STR02 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.173600
07287 1C77H STR02 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 3.693400
07289 1C79H STN01 FWD UVOL DAILY TOTAL Float (MSB 1st) 432.235700
07291 1C7BH STN01 FWD CVOL DAILY TOTAL Float (MSB 1st) 674.701900
07293 1C7DH STN01 FWD MASS DAILY TOTAL Float (MSB 1st) 33.572000
07295 1C7FH STN01 FWD ENERGY DAILY TOTAL Float (MSB 1st) 714.081400
07297 1C81H STR01 FWD UVOL DAILY TOTAL Float (MSB 1st) 184.266600
07299 1C83H STR01 FWD CVOL DAILY TOTAL Float (MSB 1st) 298.571800
07301 1C85H STR01 FWD MASS DAILY TOTAL Float (MSB 1st) 14.856400
07303 1C87H STR01 FWD ENERGY DAILY TOTAL Float (MSB 1st) 315.998200
07305 1C89H STR02 FWD UVOL DAILY TOTAL Float (MSB 1st) 247.969100
07307 1C8BH STR02 FWD CVOL DAILY TOTAL Float (MSB 1st) 376.130100
07309 1C8DH STR02 FWD MASS DAILY TOTAL Float (MSB 1st) 18.715600
07311 1C8FH STR02 FWD ENERGY DAILY TOTAL Float (MSB 1st) 398.083200
07313 1C91H STN01 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07315 1C93H STN01 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07317 1C95H STN01 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07319 1C97H STN01 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07321 1C99H STR01 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07323 1C9BH STR01 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07325 1C9DH STR01 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07327 1C9FH STR01 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07329 1CA1H STR02 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07331 1CA3H STR02 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07333 1CA5H STR02 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07335 1CA7H STR02 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07337 1CA9H STR02 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07339 1CABH STN01 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07341 1CADH STN01 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07343 1CAFH STN01 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07345 1CB1H STN01 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07347 1CB3H STR01 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07349 1CB5H STR01 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07351 1CB7H STR01 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07353 1CB9H STR01 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07355 1CBBH STR02 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07357 1CBDH STR02 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07359 1CBFH STR02 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07361 1CC1H STR02 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07363 1CC3H STR02 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07365 1CC5H STN01 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 438.589900
07367 1CC7H STN01 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 680.832700
07369 1CC9H STN01 FWD MASS MONTHLY TOTAL Float (MSB 1st) 33.877000
07371 1CCBH STN01 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 720.570000
07373 1CCDH STR01 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 187.005000
07375 1CCFH STR01 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 301.212900
07377 1CD1H STR01 FWD MASS MONTHLY TOTAL Float (MSB 1st) 14.987800
07379 1CD3H STR01 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 318.793400
07381 1CD5H STR02 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 251.584900
07383 1CD7H STR02 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 379.619800
07385 1CD9H STR02 FWD MASS MONTHLY TOTAL Float (MSB 1st) 18.889200
07387 1CDBH STR02 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 401.776600
07389 1CDDH STR02 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 401.776600
07391 1CDFH STN01 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07393 1CE1H STN01 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07395 1CE3H STN01 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07397 1CE5H STN01 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07399 1CE7H STR01 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07401 1CE9H STR01 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07403 1CEBH STR01 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07405 1CEDH STR01 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07407 1CEFH STR02 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07409 1CF1H STR02 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07411 1CF3H STR02 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07413 1CF5H STR02 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07415 1CF7H STN01 MASS FR INUSE Float (MSB 1st) 71.528044
07417 1CF9H STN01 UVOL FR INUSE Float (MSB 1st) 160.934619
07419 1CFBH STN01 CVOL FR INUSE Float (MSB 1st) 1437.508029
07421 1CFDH STN01 ENERGY FR INUSE Float (MSB 1st) 1521.409149
07423 1CFFH STR01 MASS FR INUSE Float (MSB 1st) 71.528044
07425 1D01H STR01 UVOL FR INUSE Float (MSB 1st) 160.934619
07427 1D03H STR01 CVOL FR INUSE Float (MSB 1st) 1437.508029
07429 1D05H STR01 ENERGY FR INUSE Float (MSB 1st) 1521.409149
07431 1D07H STR02 MASS FR INUSE Float (MSB 1st) 0.000000
07433 1D09H STR02 UVOL FR INUSE Float (MSB 1st) 0.000000
07435 1D0BH STR02 CVOL FR INUSE Float (MSB 1st) 0.000000
07437 1D0DH STR02 ENERGY FR INUSE Float (MSB 1st) 0.000000
07439 1D0FH STN01 CVOL FR HILIM Float (MSB 1st) 720.000000
07441 1D11H STN01 CVOL FR LOLIM Float (MSB 1st) -4.800000
07443 1D13H STR01 CVOL FR HILIM Float (MSB 1st) 3700.000000
07445 1D15H STR01 CVOL FR LOLIM Float (MSB 1st) -4.800000
07447 1D17H STR02 CVOL FR HILIM Float (MSB 1st) 3700.000000
07449 1D19H STR02 CVOL FR LOLIM Float (MSB 1st) -4.800000
07451 1D1BH STR01 BASE DENS INUSE Float (MSB 1st) 0.049758
07453 1D1DH STR01 REAL RD (SG) INUSE Float (MSB 1st) 0.650189
07455 1D1FH STR01 UPSTR COMP(Zf) INUSE Float (MSB 1st) 0.979916
07457 1D21H STR01 BASE COMP(Zb) INUSE Float (MSB 1st) 0.997460
07459 1D23H STR01 REAL CV INUSE Float (MSB 1st) 1058.365671
07461 1D25H STR01 ISENTROPIC EXP INUSE Float (MSB 1st) 1.300000
07463 1D27H STR01 VISCOSITY INUSE Float (MSB 1st) 0.010268
07465 1D29H STR01 WOBBE INDEX INUSE Float (MSB 1st) 1316.391297
07467 1D2BH STR01 UPSTR DENS INUSE Float (MSB 1st) 0.444454
07469 1D2DH STR01 UPSTR PRESS INUSE Float (MSB 1st) 120.000000
07471 1D2FH STR02 BASE DENS INUSE Float (MSB 1st) 0.049758
07473 1D31H STR02 REAL RD (SG) INUSE Float (MSB 1st) 0.650189
07475 1D33H STR02 UPSTR COMP(Zf) INUSE Float (MSB 1st) 0.979916
07477 1D35H STR02 BASE COMP(Zb) INUSE Float (MSB 1st) 0.997460
07479 1D37H STR02 REAL CV INUSE Float (MSB 1st) 1058.365671
07481 1D39H STR02 ISENTROPIC EXP INUSE Float (MSB 1st) 1.300000
07483 1D3BH STR02 VISCOSITY INUSE Float (MSB 1st) 0.010268
07485 1D3DH STR02 WOBBE INDEX INUSE Float (MSB 1st) 1316.391297
07487 1D3FH STR02 UPSTR DENS INUSE Float (MSB 1st) 0.444454
07489 1D41H STR02 UPSTR PRESS INUSE Float (MSB 1st) 120.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07491 1D43H STR01 BASE TEMP(Tb) VALUE Float (MSB 1st) 60.000000
07493 1D45H AtmP@Base (bara/psia) VALUE Float (MSB 1st) 14.730000
07495 1D47H STR01 PIPE CAL DIAM VALUE Float (MSB 1st) 4.000000
07497 1D49H STR01 ORIF CAL DIAM VALUE Float (MSB 1st) 2.000000
07499 1D4BH STR01 LOW FLOW CO VALUE Float (MSB 1st) 0.200000
07501 1D4DH STR01 PIPE CAL TEMP VALUE Float (MSB 1st) 68.000000
07503 1D4FH STR01 PIPE TEMP EXP VALUE Float (MSB 1st) 0.000006
07505 1D51H STR01 ORIF CAL TEMP VALUE Float (MSB 1st) 68.000000
07507 1D53H STR01 ORIF EXP CONST VALUE Float (MSB 1st) 0.000009
07509 1D55H STR01 VISCOSITY (Tn) VALUE Float (MSB 1st) 59.000000
07511 1D57H STR02 BASE TEMP(Tb) VALUE Float (MSB 1st) 60.000000
07513 1D59H AtmP@Base (bara/psia) VALUE Float (MSB 1st) 14.730000
07515 1D5BH STR02 PIPE CAL DIAM VALUE Float (MSB 1st) 4.000000
07517 1D5DH STR02 ORIF CAL DIAM VALUE Float (MSB 1st) 2.000000
07519 1D5FH STR02 LOW FLOW CO VALUE Float (MSB 1st) 0.200000
07521 1D61H STR02 PIPE CAL TEMP VALUE Float (MSB 1st) 68.000000
07523 1D63H STR02 PIPE TEMP EXP VALUE Float (MSB 1st) 0.000006
07525 1D65H STR02 ORIF CAL TEMP VALUE Float (MSB 1st) 68.000000
07527 1D67H STR02 ORIF EXP CONST VALUE Float (MSB 1st) 0.000009
07529 1D69H STR02 VISCOSITY (Tn) VALUE Float (MSB 1st) 59.000000
07531 1D6BH STN01 CHR SETS VALUE Float (MSB 1st) 1
07533 1D6DH STN01 MOLE SELECT OUTPUT Float (MSB 1st) 0
07535 1D6FH STN01 MOLE SELECT INPUT Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07537 1D71H STN01 CHR SLCT MOLES NITROGEN Float (MSB 1st) 0.396900
07539 1D73H STN01 CHR SLCT MOLES CO2 Float (MSB 1st) 3.897900
07541 1D75H STN01 CHR SLCT MOLES H2S Float (MSB 1st) 0.000000
07543 1D77H STN01 CHR SLCT MOLES H2O Float (MSB 1st) 0.000000
07545 1D79H STN01 CHR SLCT MOLES METHANE Float (MSB 1st) 88.771000
07547 1D7BH STN01 CHR SLCT MOLES ETHANE Float (MSB 1st) 3.957300
07549 1D7DH STN01 CHR SLCT MOLES PROPANE Float (MSB 1st) 1.904500
07551 1D7FH STN01 CHR SLCT MOLES N_BUTANE Float (MSB 1st) 0.389100
07553 1D81H STN01 CHR SLCT MOLES I_BUTANE Float (MSB 1st) 0.320100
07555 1D83H STN01 CHR SLCT MOLES N_PENTANE Float (MSB 1st) 0.089100
07557 1D85H STN01 CHR SLCT MOLES I_PENTANE Float (MSB 1st) 0.139500
07559 1D87H STN01 CHR SLCT MOLES HEXANE Float (MSB 1st) 0.134600
07561 1D89H STN01 CHR SLCT MOLES TOTAL Float (MSB 1st) 100.000000
07563 1D8BH STN01 CHR RAW MOLES C6 PLUS Float (MSB 1st) 0.000000
07565 1D8DH STN01 CHR RAW MOLES PROPANE Float (MSB 1st) 0.000000
07567 1D8FH STN01 CHR RAW MOLES iBUTANE Float (MSB 1st) 0.000000
07569 1D91H STN01 CHR RAW MOLES nBUTANE Float (MSB 1st) 0.000000
07571 1D93H STN01 CHR RAW MOLES iPENTANE Float (MSB 1st) 0.000000
07573 1D95H STN01 CHR RAW MOLES nPENTANE Float (MSB 1st) 0.000000
07575 1D97H STN01 CHR RAW MOLES NITROGEN Float (MSB 1st) 0.000000
07577 1D99H STN01 CHR RAW MOLES METHANE Float (MSB 1st) 0.000000
07579 1D9BH STN01 CHR RAW MOLES CO2 Float (MSB 1st) 0.000000
07581 1D9DH STN01 CHR RAW MOLES ETHANE Float (MSB 1st) 0.000000
07583 1D9FH STN01 CHR RAW MISC BTU DRY Float (MSB 1st) 0.000000
07585 1DA1H STN01 CHR RAW MISC BTU SAT Float (MSB 1st) 0.000000
07587 1DA3H STN01 CHR RAW MISC SG Float (MSB 1st) 0.000000
07589 1DA5H STN01 CHR RAW MISC COMPRESSIBILITY Float (MSB 1st) 0.000000
07591 1DA7H STN01 CHR RAW MISC WOBBE INDEX Float (MSB 1st) 0.000000
07593 1DA9H STN01 CHR RAW MISC TOTAL UNNORM Float (MSB 1st) 0.000000
07595 1DABH STN01 CHR RAW MISC MOLAR MAS Float (MSB 1st) 0.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07597 1DADH STN01 KEYPAD MOLES NITROGEN Float (MSB 1st) 0.396900
07599 1DAFH STN01 KEYPAD MOLES CO2 Float (MSB 1st) 3.897900
07601 1DB1H STN01 KEYPAD MOLES H2S Float (MSB 1st) 0.000000
07603 1DB3H STN01 KEYPAD MOLES H2O Float (MSB 1st) 0.000000
07605 1DB5H STN01 KEYPAD MOLES METHANE Float (MSB 1st) 88.771000
07607 1DB7H STN01 KEYPAD MOLES ETHANE Float (MSB 1st) 3.957300
07609 1DB9H STN01 KEYPAD MOLES PROPANE Float (MSB 1st) 1.904500
07611 1DBBH STN01 KEYPAD MOLES N_BUTANE Float (MSB 1st) 0.389100
07613 1DBDH STN01 KEYPAD MOLES I_BUTANE Float (MSB 1st) 0.320100
07615 1DBFH STN01 KEYPAD MOLES N_PENTANE Float (MSB 1st) 0.089100
07617 1DC1H STN01 KEYPAD MOLES I_PENTANE Float (MSB 1st) 0.139500
07619 1DC3H STN01 KEYPAD MOLES HEXANE Float (MSB 1st) 0.134600
07621 1DC5H STN01 KEYPAD MOLES TOTAL Float (MSB 1st) 100.000000
07623 1DC7H STN01 CHR K_ACCEPT VALUE Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07625 1DC9H STN01 GC INT 9026 RUN TIME Float (MSB 1st) 0
07627 1DCBH STN01 GC INT 9026 CURRENT STREAM Float (MSB 1st) 0
07629 1DCDH STN01 GC INT 9026 GC MODE Float (MSB 1st) 0
07631 1DCFH STN01 GC INT 9026 CALIBRATING Float (MSB 1st) 0
07633 1DD1H STN01 GC INT 9026 ACTIVE ALM Float (MSB 1st) 0
07635 1DD3H STN01 GC INT 9026 UNACK ALARM Float (MSB 1st) 0
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07637 1DD5H STR01 MAINT MODE VALUE Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07639 1DD7H STR01 STATUS VALUE Float (MSB 1st) 1
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07641 1DD9H STR02 MAINT MODE VALUE Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07643 1DDBH STR02 STATUS VALUE Float (MSB 1st) 2
07645 1DDDH STR01 PREV PRESS HOURLY IK Float (MSB 1st) 120.000000
07647 1DDFH STR01 PREV TEMP HOURLY IK Float (MSB 1st) 82.000000
07649 1DE1H STR01 PREV DPT HOURLY IK Float (MSB 1st) 25.000000
07651 1DE3H STR01 PREV GHV HOURLY IK Float (MSB 1st) 1058.365671
07653 1DE5H STR01 PREV UVOL FR HOURLY IK Float (MSB 1st) 160.934619
07655 1DE7H STR01 PREV CVOL FR HOURLY IK Float (MSB 1st) 1437.508029
07657 1DE9H STR01 PREV ENERGY FR HOURLY IK Float (MSB 1st) 1521.409149
07659 1DEBH STR01 PREV WOBBEINDEX HOURLY IK Float (MSB 1st) 1316.391297
07661 1DEDH STR01 PREV BASE DENS HOURLY IK Float (MSB 1st) 0.049758
07663 1DEFH STR01 PREV LINE DENS HOURLY IK Float (MSB 1st) 0.444454
07665 1DF1H STR01 PREV BASE COMP HOURLY IK Float (MSB 1st) 0.997460
07667 1DF3H STR01 PREV LINE COMP HOURLY IK Float (MSB 1st) 0.979916
07669 1DF5H STR01 PREV SG HOURLY IK Float (MSB 1st) 0.650189
07671 1DF7H STR01 PREV PRESS DAILY IK Float (MSB 1st) 0.000000
07673 1DF9H STR01 PREV TEMP DAILY IK Float (MSB 1st) 0.000000
07675 1DFBH STR01 PREV DPT DAILY IK Float (MSB 1st) 0.000000
07677 1DFDH STR01 PREV GHV DAILY IK Float (MSB 1st) 0.000000
07679 1DFFH STR01 PREV UVOL FR DAILY IK Float (MSB 1st) 0.000000
07681 1E01H STR01 PREV CVOL FR DAILY IK Float (MSB 1st) 0.000000
07683 1E03H STR01 PREV ENERGY FR DAILY IK Float (MSB 1st) 0.000000
07685 1E05H STR01 PREV WOBBEINDEX DAILY IK Float (MSB 1st) 0.000000
07687 1E07H STR01 PREV BASE DENS DAILY IK Float (MSB 1st) 0.000000
07689 1E09H STR01 PREV LINE DENS DAILY IK Float (MSB 1st) 0.000000
07691 1E0BH STR01 PREV BASE COMP DAILY IK Float (MSB 1st) 0.000000
07693 1E0DH STR01 PREV LINE COMP DAILY IK Float (MSB 1st) 0.000000
07695 1E0FH STR01 PREV SG DAILY IK Float (MSB 1st) 0.000000
07697 1E11H STR01 PREV PRESS MONTHLY IK Float (MSB 1st) 0.000000
07699 1E13H STR01 PREV TEMP MONTHLY IK Float (MSB 1st) 0.000000
07701 1E15H STR01 PREV DPT MONTHLY IK Float (MSB 1st) 0.000000
07703 1E17H STR01 PREV GHV MONTHLY IK Float (MSB 1st) 0.000000
07705 1E19H STR01 PREV UVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07707 1E1BH STR01 PREV CVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07709 1E1DH STR01 PREV ENERGY FR MONTHLY IK Float (MSB 1st) 0.000000
07711 1E1FH STR01 PREV WOBBEINDEX MONTHLY IK Float (MSB 1st) 0.000000
07713 1E21H STR01 PREV BASE DENS MONTHLY IK Float (MSB 1st) 0.000000
07715 1E23H STR01 PREV LINE DENS MONTHLY IK Float (MSB 1st) 0.000000
07717 1E25H STR01 PREV BASE COMP MONTHLY IK Float (MSB 1st) 0.000000
07719 1E27H STR01 PREV LINE COMP MONTHLY IK Float (MSB 1st) 0.000000
07721 1E29H STR01 PREV SG MONTHLY IK Float (MSB 1st) 0.000000
07723 1E2BH STR02 PREV PRESS HOURLY IK Float (MSB 1st) 0.000000
07725 1E2DH STR02 PREV TEMP HOURLY IK Float (MSB 1st) 0.000000
07727 1E2FH STR02 PREV DPT HOURLY IK Float (MSB 1st) 0.000000
07729 1E31H STR02 PREV GHV HOURLY IK Float (MSB 1st) 0.000000
07731 1E33H STR02 PREV UVOL FR HOURLY IK Float (MSB 1st) 0.000000
07733 1E35H STR02 PREV CVOL FR HOURLY IK Float (MSB 1st) 0.000000
07735 1E37H STR02 PREV ENERGY FR HOURLY IK Float (MSB 1st) 0.000000
07737 1E39H STR02 PREV WOBBEINDEX HOURLY IK Float (MSB 1st) 0.000000
07739 1E3BH STR02 PREV BASE DENS HOURLY IK Float (MSB 1st) 0.000000
07741 1E3DH STR02 PREV LINE DENS HOURLY IK Float (MSB 1st) 0.000000
07743 1E3FH STR02 PREV BASE COMP HOURLY IK Float (MSB 1st) 0.000000
07745 1E41H STR02 PREV LINE COMP HOURLY IK Float (MSB 1st) 0.000000
07747 1E43H STR02 PREV SG HOURLY IK Float (MSB 1st) 0.000000
07749 1E45H STR02 PREV PRESS DAILY IK Float (MSB 1st) 0.000000
07751 1E47H STR02 PREV TEMP DAILY IK Float (MSB 1st) 0.000000
07753 1E49H STR02 PREV DPT DAILY IK Float (MSB 1st) 0.000000
07755 1E4BH STR02 PREV GHV DAILY IK Float (MSB 1st) 0.000000
07757 1E4DH STR02 PREV UVOL FR DAILY IK Float (MSB 1st) 0.000000
07759 1E4FH STR02 PREV CVOL FR DAILY IK Float (MSB 1st) 0.000000
07761 1E51H STR02 PREV ENERGY FR DAILY IK Float (MSB 1st) 0.000000
07763 1E53H STR02 PREV WOBBEINDEX DAILY IK Float (MSB 1st) 0.000000
07765 1E55H STR02 PREV BASE DENS DAILY IK Float (MSB 1st) 0.000000
07767 1E57H STR02 PREV LINE DENS DAILY IK Float (MSB 1st) 0.000000
07769 1E59H STR02 PREV BASE COMP DAILY IK Float (MSB 1st) 0.000000
07771 1E5BH STR02 PREV LINE COMP DAILY IK Float (MSB 1st) 0.000000
07773 1E5DH STR02 PREV SG DAILY IK Float (MSB 1st) 0.000000
07775 1E5FH STR02 PREV PRESS MONTHLY IK Float (MSB 1st) 0.000000
07777 1E61H STR02 PREV TEMP MONTHLY IK Float (MSB 1st) 0.000000
07779 1E63H STR02 PREV DPT MONTHLY IK Float (MSB 1st) 0.000000
07781 1E65H STR02 PREV GHV MONTHLY IK Float (MSB 1st) 0.000000
07783 1E67H STR02 PREV UVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07785 1E69H STR02 PREV CVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07787 1E6BH STR02 PREV ENERGY FR MONTHLY IK Float (MSB 1st) 0.000000
07789 1E6DH STR02 PREV WOBBEINDEX MONTHLY IK Float (MSB 1st) 0.000000
07791 1E6FH STR02 PREV BASE DENS MONTHLY IK Float (MSB 1st) 0.000000
07793 1E71H STR02 PREV LINE DENS MONTHLY IK Float (MSB 1st) 0.000000
07795 1E73H STR02 PREV BASE COMP MONTHLY IK Float (MSB 1st) 0.000000
07797 1E75H STR02 PREV LINE COMP MONTHLY IK Float (MSB 1st) 0.000000
07799 1E77H STR02 PREV SG MONTHLY IK Float (MSB 1st) 0.000000
07801 1E79H STR01 GCFWA HOURLY NITROGEN Float (MSB 1st) 0.396900
07803 1E7BH STR01 GCFWA HOURLY CO2 Float (MSB 1st) 3.897900
07805 1E7DH STR01 GCFWA HOURLY METHANE Float (MSB 1st) 88.771000
07807 1E7FH STR01 GCFWA HOURLY ETHANE Float (MSB 1st) 3.957300
07809 1E81H STR01 GCFWA HOURLY PROPANE Float (MSB 1st) 1.904500
07811 1E83H STR01 GCFWA HOURLY N_BUTANE Float (MSB 1st) 0.389100
07813 1E85H STR01 GCFWA HOURLY I_BUTANE Float (MSB 1st) 0.320100
07815 1E87H STR01 GCFWA HOURLY N_PENTANE Float (MSB 1st) 0.089100
07817 1E89H STR01 GCFWA HOURLY I_PENTANE Float (MSB 1st) 0.139500
07819 1E8BH STR01 GCFWA HOURLY HEXANE Float (MSB 1st) 0.134600
07821 1E8DH STR01 GCFWA HOURLY TOTAL Float (MSB 1st) 100.000000
07823 1E8FH STR02 GCFWA DAILY NITROGEN Float (MSB 1st) 0.000000
07825 1E91H STR02 GCFWA DAILY CO2 Float (MSB 1st) 0.000000
07827 1E93H STR02 GCFWA DAILY METHANE Float (MSB 1st) 0.000000
07829 1E95H STR02 GCFWA DAILY ETHANE Float (MSB 1st) 0.000000
07831 1E97H STR02 GCFWA DAILY PROPANE Float (MSB 1st) 0.000000
07833 1E99H STR02 GCFWA DAILY N_BUTANE Float (MSB 1st) 0.000000
07835 1E9BH STR02 GCFWA DAILY I_BUTANE Float (MSB 1st) 0.000000
07837 1E9DH STR02 GCFWA DAILY N_PENTANE Float (MSB 1st) 0.000000
07839 1E9FH STR02 GCFWA DAILY I_PENTANE Float (MSB 1st) 0.000000
07841 1EA1H STR02 GCFWA DAILY HEXANE Float (MSB 1st) 0.000000
07843 1EA3H STR02 GCFWA DAILY TOTAL Float (MSB 1st) 0.000000
07845 1EA5H STR02 GCFWA MONTHLY NITROGEN Float (MSB 1st) 0.000000
07847 1EA7H STR02 GCFWA MONTHLY CO2 Float (MSB 1st) 0.000000
07849 1EA9H STR02 GCFWA MONTHLY METHANE Float (MSB 1st) 0.000000
07851 1EABH STR02 GCFWA MONTHLY ETHANE Float (MSB 1st) 0.000000
07853 1EADH STR02 GCFWA MONTHLY PROPANE Float (MSB 1st) 0.000000
07855 1EAFH STR02 GCFWA MONTHLY N_BUTANE Float (MSB 1st) 0.000000
07857 1EB1H STR02 GCFWA MONTHLY I_BUTANE Float (MSB 1st) 0.000000
07859 1EB3H STR02 GCFWA MONTHLY N_PENTANE Float (MSB 1st) 0.000000
07861 1EB5H STR02 GCFWA MONTHLY I_PENTANE Float (MSB 1st) 0.000000
07863 1EB7H STR02 GCFWA MONTHLY HEXANE Float (MSB 1st) 0.000000
07865 1EB9H STR02 GCFWA MONTHLY TOTAL Float (MSB 1st) 0.000000
07867 1EBBH TIME AND DATE CUR.YEAR Float (MSB 1st) 2025
07869 1EBDH TIME AND DATE CUR.MONTH Float (MSB 1st) 7
07871 1EBFH TIME AND DATE CUR.DAY Float (MSB 1st) 21
07873 1EC1H TIME AND DATE CUR.HOUR Float (MSB 1st) 21
07875 1EC3H TIME AND DATE CUR.MINUTE Float (MSB 1st) 10
07877 1EC5H TIME AND DATE CUR.SECOND Float (MSB 1st) 59
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07879 1EC7H TIME AND DATE DLOAD YEAR Float (MSB 1st) 2025
07881 1EC9H TIME AND DATE DLOAD MONTH Float (MSB 1st) 7
07883 1ECBH TIME AND DATE DLOAD DAY Float (MSB 1st) 21
07885 1ECDH TIME AND DATE DLOAD HOUR Float (MSB 1st) 20
07887 1ECFH TIME AND DATE DLOAD MINUTE Float (MSB 1st) 55
07889 1ED1H TIME AND DATE DLOAD SECOND Float (MSB 1st) 19
07891 1ED3H DLOAD TIME ACCEPT VALUE Float (MSB 1st) 0
07893 1ED5H SYS PEER STAT OUTPUT Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07895 1ED7H SYS PEER STAT INPUT Float (MSB 1st) 3
07897 1ED9H STN01 GC INT 9026 RUN TIME Float (MSB 1st) 0
07899 1EDBH STN01 GC INT 9026 CURRENT STREAM Float (MSB 1st) 0
07901 1EDDH STN01 GC INT 9026 GC MODE Float (MSB 1st) 0
07903 1EDFH STN01 GC INT 9026 CALIBRATING Float (MSB 1st) 0
07905 1EE1H STN01 GC INT 9026 ACTIVE ALM Float (MSB 1st) 0
07907 1EE3H STN01 GC INT 9026 UNACK ALARM Float (MSB 1st) 0
[EVENTING MODE : ALL]
[SECURITY LEVEL : READ / WRITE]
07909 1EE5H SDV VLV OUTPUT Float (MSB 1st) 0
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07911 1EE7H SDV VLV INPUT Float (MSB 1st) 0
[EVENTING MODE : CHANGES]
07913 1EE9H ESD BUTTON INPUT Float (MSB 1st) 1
[SECURITY LEVEL : READ / WRITE]
07915 1EEBH PT-12501-04 HIHILIM Float (MSB 1st) 450.000000
07917 1EEDH PT-12501-04 HILIM Float (MSB 1st) 400.000000
07919 1EEFH PT-12501-04 LOLIM Float (MSB 1st) 60.000000
07921 1EF1H PT-12501-04 LOLOLIM Float (MSB 1st) 30.000000
07923 1EF3H PT-12501-05 HIHILIM Float (MSB 1st) 150.000000
07925 1EF5H PT-12501-05 HILIM Float (MSB 1st) 120.000000
07927 1EF7H PT-12501-05 LOLIM Float (MSB 1st) 50.000000
07929 1EF9H PT-12501-05 LOLOLIM Float (MSB 1st) 25.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07931 1EFBH STN01 CVOL FR RAW Float (MSB 1st) 1437.508029
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07933 1EFDH STN01 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07935 1EFFH STN01 CVOL FR HISCALE Float (MSB 1st) 5000.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07937 1F01H STR01 CVOL FR RAW Float (MSB 1st) 1437.508029
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07939 1F03H STR01 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07941 1F05H STR01 CVOL FR HISCALE Float (MSB 1st) 5000.000000
[EVENTING MODE : DISABLED]
[SECURITY LEVEL : READ ONLY]
07943 1F07H STR02 CVOL FR RAW Float (MSB 1st) 0.000000
[EVENTING MODE : CHANGES]
[SECURITY LEVEL : READ / WRITE]
07945 1F09H STR02 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07947 1F0BH STR02 CVOL FR HISCALE Float (MSB 1st) 5000.000000
07949 1F0DH ESD BUTTON OUTPUT Float (MSB 1st) 1

## Maps (2)
07001 1B59H PT-12501-01 MODE Float (MSB 1st) 4
07003 1B5BH PT-12501-01 INUSE Float (MSB 1st) 120.000000
07005 1B5DH PT-12501-01 KEYPAD Float (MSB 1st) 120.000000
07007 1B5FH PT-12501-01 MEASURED Float (MSB 1st) -124.986168
07009 1B61H PT-12501-01 CURRENT Float (MSB 1st) 0.000443
07011 1B63H PT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07013 1B65H PT-12501-01 HISCALE Float (MSB 1st) 500.000000
07015 1B67H PT-12501-01 HILIM Float (MSB 1st) 200.000000
07017 1B69H PT-12501-01 LOLIM Float (MSB 1st) 60.000000
07019 1B6BH DPT-12501-01 MODE Float (MSB 1st) 4
07021 1B6DH DPT-12501-01 INUSE Float (MSB 1st) 0.000000
07023 1B6FH DPT-12501-01 KEYPAD Float (MSB 1st) 0.000000
07025 1B71H DPT-12501-01 MEASURED Float (MSB 1st) -49.993749
07027 1B73H DPT-12501-01 CURRENT Float (MSB 1st) 0.000500
07029 1B75H DPT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07031 1B77H DPT-12501-01 HISCALE Float (MSB 1st) 200.000000
07033 1B79H DPT-12501-01 HILIM Float (MSB 1st) 200.000000
07035 1B7BH DPT-12501-01 LOLIM Float (MSB 1st) -2.000000
07037 1B7DH TT-12501-01 MODE Float (MSB 1st) 4
07039 1B7FH TT-12501-01 INUSE Float (MSB 1st) 82.000000
07041 1B81H TT-12501-01 KEYPAD Float (MSB 1st) 82.000000
07043 1B83H TT-12501-01 MEASURED Float (MSB 1st) -37.495089
07045 1B85H TT-12501-01 CURRENT Float (MSB 1st) 0.000524
07047 1B87H TT-12501-01 LOSCALE Float (MSB 1st) 0.000000
07049 1B89H TT-12501-01 HISCALE Float (MSB 1st) 150.000000
07051 1B8BH TT-12501-01 HILIM Float (MSB 1st) 86.000000
07053 1B8DH TT-12501-01 LOLIM Float (MSB 1st) 75.000000
07055 1B8FH PT-12501-04 MODE Float (MSB 1st) 4
07057 1B91H PT-12501-04 INUSE Float (MSB 1st) 300.000000
07059 1B93H PT-12501-04 KEYPAD Float (MSB 1st) 300.000000
07061 1B95H PT-12501-04 MEASURED Float (MSB 1st) -124.983837
07063 1B97H PT-12501-04 CURRENT Float (MSB 1st) 0.000517
07065 1B99H PT-12501-04 LOSCALE Float (MSB 1st) 0.000000
07067 1B9BH PT-12501-04 HISCALE Float (MSB 1st) 500.000000
07069 1B9DH PT-12501-04 HILIM Float (MSB 1st) 400.000000
07071 1B9FH PT-12501-04 LOLIM Float (MSB 1st) 60.000000
07073 1BA1H PT-12501-05 MODE Float (MSB 1st) 4
07075 1BA3H PT-12501-05 INUSE Float (MSB 1st) 200.000000
07077 1BA5H PT-12501-05 KEYPAD Float (MSB 1st) 200.000000
07079 1BA7H PT-12501-05 MEASURED Float (MSB 1st) -124.982040
07081 1BA9H PT-12501-05 CURRENT Float (MSB 1st) 0.000575
07083 1BABH PT-12501-05 LOSCALE Float (MSB 1st) 0.000000
07085 1BADH PT-12501-05 HISCALE Float (MSB 1st) 500.000000
07087 1BAFH PT-12501-05 HILIM Float (MSB 1st) 120.000000
07089 1BB1H PT-12501-05 LOLIM Float (MSB 1st) 50.000000
07091 1BB3H PT-12501-02 MODE Float (MSB 1st) 4
07093 1BB5H PT-12501-02 INUSE Float (MSB 1st) 120.000000
07095 1BB7H PT-12501-02 KEYPAD Float (MSB 1st) 120.000000
07097 1BB9H PT-12501-02 MEASURED Float (MSB 1st) -124.982501
07099 1BBBH PT-12501-02 CURRENT Float (MSB 1st) 0.000560
07101 1BBDH PT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07103 1BBFH PT-12501-02 HISCALE Float (MSB 1st) 500.000000
07105 1BC1H PT-12501-02 HILIM Float (MSB 1st) 200.000000
07107 1BC3H PT-12501-02 LOLIM Float (MSB 1st) 60.000000
07109 1BC5H DPT-12501-02 MODE Float (MSB 1st) 4
07111 1BC7H DPT-12501-02 INUSE Float (MSB 1st) 0.000000
07113 1BC9H DPT-12501-02 KEYPAD Float (MSB 1st) 0.000000
07115 1BCBH DPT-12501-02 MEASURED Float (MSB 1st) -49.993800
07117 1BCDH DPT-12501-02 CURRENT Float (MSB 1st) 0.000496
07119 1BCFH DPT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07121 1BD1H DPT-12501-02 HISCALE Float (MSB 1st) 200.000000
07123 1BD3H DPT-12501-02 HILIM Float (MSB 1st) 200.000000
07125 1BD5H DPT-12501-02 LOLIM Float (MSB 1st) -2.000000
07127 1BD7H TT-12501-02 MODE Float (MSB 1st) 4
07129 1BD9H TT-12501-02 INUSE Float (MSB 1st) 82.000000
07131 1BDBH TT-12501-02 KEYPAD Float (MSB 1st) 82.000000
07133 1BDDH TT-12501-02 MEASURED Float (MSB 1st) -37.493839
07135 1BDFH TT-12501-02 CURRENT Float (MSB 1st) 0.000657
07137 1BE1H TT-12501-02 LOSCALE Float (MSB 1st) 0.000000
07139 1BE3H TT-12501-02 HISCALE Float (MSB 1st) 150.000000
07141 1BE5H TT-12501-02 HILIM Float (MSB 1st) 86.000000
07143 1BE7H TT-12501-02 LOLIM Float (MSB 1st) 75.000000
07145 1BE9H STN01 FWD UVOL TOTAL Float (MSB 1st) 438.589200
07147 1BEBH STN01 FWD CVOL TOTAL Float (MSB 1st) 680.826800
07149 1BEDH STN01 FWD MASS TOTAL Float (MSB 1st) 33.876700
07151 1BEFH STN01 FWD ENERGY TOTAL Float (MSB 1st) 720.563800
07153 1BF1H STR01 FWD UVOL TOTAL Float (MSB 1st) 187.004300
07155 1BF3H STR01 FWD CVOL TOTAL Float (MSB 1st) 301.207000
07157 1BF5H STR01 FWD MASS TOTAL Float (MSB 1st) 14.987500
07159 1BF7H STR01 FWD ENERGY TOTAL Float (MSB 1st) 318.787200
07161 1BF9H STR02 FWD UVOL TOTAL Float (MSB 1st) 251.584900
07163 1BFBH STR02 FWD CVOL TOTAL Float (MSB 1st) 379.619800
07165 1BFDH STR02 FWD MASS TOTAL Float (MSB 1st) 18.889200
07167 1BFFH STR02 FWD ENERGY TOTAL Float (MSB 1st) 401.776600
07169 1C01H STN01 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 2.807100
07171 1C03H STN01 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 25.073500
07173 1C05H STN01 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 1.247600
07175 1C07H STN01 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 26.536900
07177 1C09H STR01 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 2.807100
07179 1C0BH STR01 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 25.073500
07181 1C0DH STR01 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 1.247600
07183 1C0FH STR01 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 26.536900
07185 1C11H STR02 FWD UVOL HOURLY PREVIOUS Float (MSB 1st) 0.000000
07187 1C13H STR02 FWD CVOL HOURLY PREVIOUS Float (MSB 1st) 0.000000
07189 1C15H STR02 FWD MASS HOURLY PREVIOUS Float (MSB 1st) 0.000000
07191 1C17H STR02 FWD ENERGY HOURLY PREVIOUS Float (MSB 1st) 0.000000
07193 1C19H STN01 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 437.362500
07195 1C1BH STN01 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 669.869200
07197 1C1DH STN01 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 33.331500
07199 1C1FH STN01 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 708.966600
07201 1C21H STR01 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 185.777600
07203 1C23H STR01 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 290.249400
07205 1C25H STR01 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 14.442300
07207 1C27H STR01 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 307.190000
07209 1C29H STR02 FWD UVOL HOURLY SNAPSHOT Float (MSB 1st) 251.584900
07211 1C2BH STR02 FWD CVOL HOURLY SNAPSHOT Float (MSB 1st) 379.619800
07213 1C2DH STR02 FWD MASS HOURLY SNAPSHOT Float (MSB 1st) 18.889200
07215 1C2FH STR02 FWD ENERGY HOURLY SNAPSHOT Float (MSB 1st) 401.776600
07217 1C31H STN01 FWD UVOL HOURLY TOTAL Float (MSB 1st) 1.226700
07219 1C33H STN01 FWD CVOL HOURLY TOTAL Float (MSB 1st) 10.957600
07221 1C35H STN01 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.545200
07223 1C37H STN01 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 11.597200
07225 1C39H STR01 FWD UVOL HOURLY TOTAL Float (MSB 1st) 1.226700
07227 1C3BH STR01 FWD CVOL HOURLY TOTAL Float (MSB 1st) 10.957600
07229 1C3DH STR01 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.545200
07231 1C3FH STR01 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 11.597200
07233 1C41H STR02 FWD UVOL HOURLY TOTAL Float (MSB 1st) 0.000000
07235 1C43H STR02 FWD CVOL HOURLY TOTAL Float (MSB 1st) 0.000000
07237 1C45H STR02 FWD MASS HOURLY TOTAL Float (MSB 1st) 0.000000
07239 1C47H STR02 FWD ENERGY HOURLY TOTAL Float (MSB 1st) 0.000000
07241 1C49H STN01 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 6.354200
07243 1C4BH STN01 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 6.130800
07245 1C4DH STN01 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.305000
07247 1C4FH STN01 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 6.488600
07249 1C51H STR01 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 2.738400
07251 1C53H STR01 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 2.641100
07253 1C55H STR01 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.131400
07255 1C57H STR01 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 2.795200
07257 1C59H STR02 FWD UVOL DAILY PREVIOUS Float (MSB 1st) 3.615800
07259 1C5BH STR02 FWD CVOL DAILY PREVIOUS Float (MSB 1st) 3.489700
07261 1C5DH STR02 FWD MASS DAILY PREVIOUS Float (MSB 1st) 0.173600
07263 1C5FH STR02 FWD ENERGY DAILY PREVIOUS Float (MSB 1st) 3.693400
07265 1C61H STN01 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 6.354200
07267 1C63H STN01 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 6.130800
07269 1C65H STN01 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.305000
07271 1C67H STN01 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 6.488600
07273 1C69H STR01 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 2.738400
07275 1C6BH STR01 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 2.641100
07277 1C6DH STR01 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.131400
07279 1C6FH STR01 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 2.795200
07281 1C71H STR02 FWD UVOL DAILY SNAPSHOT Float (MSB 1st) 3.615800
07283 1C73H STR02 FWD CVOL DAILY SNAPSHOT Float (MSB 1st) 3.489700
07285 1C75H STR02 FWD MASS DAILY SNAPSHOT Float (MSB 1st) 0.173600
07287 1C77H STR02 FWD ENERGY DAILY SNAPSHOT Float (MSB 1st) 3.693400
07289 1C79H STN01 FWD UVOL DAILY TOTAL Float (MSB 1st) 432.235700
07291 1C7BH STN01 FWD CVOL DAILY TOTAL Float (MSB 1st) 674.701900
07293 1C7DH STN01 FWD MASS DAILY TOTAL Float (MSB 1st) 33.572000
07295 1C7FH STN01 FWD ENERGY DAILY TOTAL Float (MSB 1st) 714.081400
07297 1C81H STR01 FWD UVOL DAILY TOTAL Float (MSB 1st) 184.266600
07299 1C83H STR01 FWD CVOL DAILY TOTAL Float (MSB 1st) 298.571800
07301 1C85H STR01 FWD MASS DAILY TOTAL Float (MSB 1st) 14.856400
07303 1C87H STR01 FWD ENERGY DAILY TOTAL Float (MSB 1st) 315.998200
07305 1C89H STR02 FWD UVOL DAILY TOTAL Float (MSB 1st) 247.969100
07307 1C8BH STR02 FWD CVOL DAILY TOTAL Float (MSB 1st) 376.130100
07309 1C8DH STR02 FWD MASS DAILY TOTAL Float (MSB 1st) 18.715600
07311 1C8FH STR02 FWD ENERGY DAILY TOTAL Float (MSB 1st) 398.083200
07313 1C91H STN01 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07315 1C93H STN01 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07317 1C95H STN01 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07319 1C97H STN01 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07321 1C99H STR01 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07323 1C9BH STR01 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07325 1C9DH STR01 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07327 1C9FH STR01 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07329 1CA1H STR02 FWD UVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07331 1CA3H STR02 FWD CVOL MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07333 1CA5H STR02 FWD MASS MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07335 1CA7H STR02 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07337 1CA9H STR02 FWD ENERGY MONTHLY PREVIOUS Float (MSB 1st) 0.000000
07339 1CABH STN01 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07341 1CADH STN01 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07343 1CAFH STN01 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07345 1CB1H STN01 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07347 1CB3H STR01 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07349 1CB5H STR01 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07351 1CB7H STR01 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07353 1CB9H STR01 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07355 1CBBH STR02 FWD UVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07357 1CBDH STR02 FWD CVOL MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07359 1CBFH STR02 FWD MASS MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07361 1CC1H STR02 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07363 1CC3H STR02 FWD ENERGY MONTHLY SNAPSHOT Float (MSB 1st) 0.000000
07365 1CC5H STN01 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 438.589900
07367 1CC7H STN01 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 680.832700
07369 1CC9H STN01 FWD MASS MONTHLY TOTAL Float (MSB 1st) 33.877000
07371 1CCBH STN01 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 720.570000
07373 1CCDH STR01 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 187.005000
07375 1CCFH STR01 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 301.212900
07377 1CD1H STR01 FWD MASS MONTHLY TOTAL Float (MSB 1st) 14.987800
07379 1CD3H STR01 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 318.793400
07381 1CD5H STR02 FWD UVOL MONTHLY TOTAL Float (MSB 1st) 251.584900
07383 1CD7H STR02 FWD CVOL MONTHLY TOTAL Float (MSB 1st) 379.619800
07385 1CD9H STR02 FWD MASS MONTHLY TOTAL Float (MSB 1st) 18.889200
07387 1CDBH STR02 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 401.776600
07389 1CDDH STR02 FWD ENERGY MONTHLY TOTAL Float (MSB 1st) 401.776600
07391 1CDFH STN01 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07393 1CE1H STN01 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07395 1CE3H STN01 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07397 1CE5H STN01 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07399 1CE7H STR01 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07401 1CE9H STR01 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07403 1CEBH STR01 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07405 1CEDH STR01 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07407 1CEFH STR02 FWD UVOL MAINT TOTAL Float (MSB 1st) 0.000000
07409 1CF1H STR02 FWD CVOL MAINT TOTAL Float (MSB 1st) 0.000000
07411 1CF3H STR02 FWD MASS MAINT TOTAL Float (MSB 1st) 0.000000
07413 1CF5H STR02 FWD ENERGY MAINT TOTAL Float (MSB 1st) 0.000000
07415 1CF7H STN01 MASS FR INUSE Float (MSB 1st) 71.528044
07417 1CF9H STN01 UVOL FR INUSE Float (MSB 1st) 160.934619
07419 1CFBH STN01 CVOL FR INUSE Float (MSB 1st) 1437.508029
07421 1CFDH STN01 ENERGY FR INUSE Float (MSB 1st) 1521.409149
07423 1CFFH STR01 MASS FR INUSE Float (MSB 1st) 71.528044
07425 1D01H STR01 UVOL FR INUSE Float (MSB 1st) 160.934619
07427 1D03H STR01 CVOL FR INUSE Float (MSB 1st) 1437.508029
07429 1D05H STR01 ENERGY FR INUSE Float (MSB 1st) 1521.409149
07431 1D07H STR02 MASS FR INUSE Float (MSB 1st) 0.000000
07433 1D09H STR02 UVOL FR INUSE Float (MSB 1st) 0.000000
07435 1D0BH STR02 CVOL FR INUSE Float (MSB 1st) 0.000000
07437 1D0DH STR02 ENERGY FR INUSE Float (MSB 1st) 0.000000
07439 1D0FH STN01 CVOL FR HILIM Float (MSB 1st) 720.000000
07441 1D11H STN01 CVOL FR LOLIM Float (MSB 1st) -4.800000
07443 1D13H STR01 CVOL FR HILIM Float (MSB 1st) 3700.000000
07445 1D15H STR01 CVOL FR LOLIM Float (MSB 1st) -4.800000
07447 1D17H STR02 CVOL FR HILIM Float (MSB 1st) 3700.000000
07449 1D19H STR02 CVOL FR LOLIM Float (MSB 1st) -4.800000
07451 1D1BH STR01 BASE DENS INUSE Float (MSB 1st) 0.049758
07453 1D1DH STR01 REAL RD (SG) INUSE Float (MSB 1st) 0.650189
07455 1D1FH STR01 UPSTR COMP(Zf) INUSE Float (MSB 1st) 0.979916
07457 1D21H STR01 BASE COMP(Zb) INUSE Float (MSB 1st) 0.997460
07459 1D23H STR01 REAL CV INUSE Float (MSB 1st) 1058.365671
07461 1D25H STR01 ISENTROPIC EXP INUSE Float (MSB 1st) 1.300000
07463 1D27H STR01 VISCOSITY INUSE Float (MSB 1st) 0.010268
07465 1D29H STR01 WOBBE INDEX INUSE Float (MSB 1st) 1316.391297
07467 1D2BH STR01 UPSTR DENS INUSE Float (MSB 1st) 0.444454
07469 1D2DH STR01 UPSTR PRESS INUSE Float (MSB 1st) 120.000000
07471 1D2FH STR02 BASE DENS INUSE Float (MSB 1st) 0.049758
07473 1D31H STR02 REAL RD (SG) INUSE Float (MSB 1st) 0.650189
07475 1D33H STR02 UPSTR COMP(Zf) INUSE Float (MSB 1st) 0.979916
07477 1D35H STR02 BASE COMP(Zb) INUSE Float (MSB 1st) 0.997460
07479 1D37H STR02 REAL CV INUSE Float (MSB 1st) 1058.365671
07481 1D39H STR02 ISENTROPIC EXP INUSE Float (MSB 1st) 1.300000
07483 1D3BH STR02 VISCOSITY INUSE Float (MSB 1st) 0.010268
07485 1D3DH STR02 WOBBE INDEX INUSE Float (MSB 1st) 1316.391297
07487 1D3FH STR02 UPSTR DENS INUSE Float (MSB 1st) 0.444454
07489 1D41H STR02 UPSTR PRESS INUSE Float (MSB 1st) 120.000000
07491 1D43H STR01 BASE TEMP(Tb) VALUE Float (MSB 1st) 60.000000
07493 1D45H AtmP@Base (bara/psia) VALUE Float (MSB 1st) 14.730000
07495 1D47H STR01 PIPE CAL DIAM VALUE Float (MSB 1st) 4.000000
07497 1D49H STR01 ORIF CAL DIAM VALUE Float (MSB 1st) 2.000000
07499 1D4BH STR01 LOW FLOW CO VALUE Float (MSB 1st) 0.200000
07501 1D4DH STR01 PIPE CAL TEMP VALUE Float (MSB 1st) 68.000000
07503 1D4FH STR01 PIPE TEMP EXP VALUE Float (MSB 1st) 0.000006
07505 1D51H STR01 ORIF CAL TEMP VALUE Float (MSB 1st) 68.000000
07507 1D53H STR01 ORIF EXP CONST VALUE Float (MSB 1st) 0.000009
07509 1D55H STR01 VISCOSITY (Tn) VALUE Float (MSB 1st) 59.000000
07511 1D57H STR02 BASE TEMP(Tb) VALUE Float (MSB 1st) 60.000000
07513 1D59H AtmP@Base (bara/psia) VALUE Float (MSB 1st) 14.730000
07515 1D5BH STR02 PIPE CAL DIAM VALUE Float (MSB 1st) 4.000000
07517 1D5DH STR02 ORIF CAL DIAM VALUE Float (MSB 1st) 2.000000
07519 1D5FH STR02 LOW FLOW CO VALUE Float (MSB 1st) 0.200000
07521 1D61H STR02 PIPE CAL TEMP VALUE Float (MSB 1st) 68.000000
07523 1D63H STR02 PIPE TEMP EXP VALUE Float (MSB 1st) 0.000006
07525 1D65H STR02 ORIF CAL TEMP VALUE Float (MSB 1st) 68.000000
07527 1D67H STR02 ORIF EXP CONST VALUE Float (MSB 1st) 0.000009
07529 1D69H STR02 VISCOSITY (Tn) VALUE Float (MSB 1st) 59.000000
07531 1D6BH STN01 CHR SETS VALUE Float (MSB 1st) 1
07533 1D6DH STN01 MOLE SELECT OUTPUT Float (MSB 1st) 0
07535 1D6FH STN01 MOLE SELECT INPUT Float (MSB 1st) 0
07537 1D71H STN01 CHR SLCT MOLES NITROGEN Float (MSB 1st) 0.396900
07539 1D73H STN01 CHR SLCT MOLES CO2 Float (MSB 1st) 3.897900
07541 1D75H STN01 CHR SLCT MOLES H2S Float (MSB 1st) 0.000000
07543 1D77H STN01 CHR SLCT MOLES H2O Float (MSB 1st) 0.000000
07545 1D79H STN01 CHR SLCT MOLES METHANE Float (MSB 1st) 88.771000
07547 1D7BH STN01 CHR SLCT MOLES ETHANE Float (MSB 1st) 3.957300
07549 1D7DH STN01 CHR SLCT MOLES PROPANE Float (MSB 1st) 1.904500
07551 1D7FH STN01 CHR SLCT MOLES N_BUTANE Float (MSB 1st) 0.389100
07553 1D81H STN01 CHR SLCT MOLES I_BUTANE Float (MSB 1st) 0.320100
07555 1D83H STN01 CHR SLCT MOLES N_PENTANE Float (MSB 1st) 0.089100
07557 1D85H STN01 CHR SLCT MOLES I_PENTANE Float (MSB 1st) 0.139500
07559 1D87H STN01 CHR SLCT MOLES HEXANE Float (MSB 1st) 0.134600
07561 1D89H STN01 CHR SLCT MOLES TOTAL Float (MSB 1st) 100.000000
07563 1D8BH STN01 CHR RAW MOLES C6 PLUS Float (MSB 1st) 0.000000
07565 1D8DH STN01 CHR RAW MOLES PROPANE Float (MSB 1st) 0.000000
07567 1D8FH STN01 CHR RAW MOLES iBUTANE Float (MSB 1st) 0.000000
07569 1D91H STN01 CHR RAW MOLES nBUTANE Float (MSB 1st) 0.000000
07571 1D93H STN01 CHR RAW MOLES iPENTANE Float (MSB 1st) 0.000000
07573 1D95H STN01 CHR RAW MOLES nPENTANE Float (MSB 1st) 0.000000
07575 1D97H STN01 CHR RAW MOLES NITROGEN Float (MSB 1st) 0.000000
07577 1D99H STN01 CHR RAW MOLES METHANE Float (MSB 1st) 0.000000
07579 1D9BH STN01 CHR RAW MOLES CO2 Float (MSB 1st) 0.000000
07581 1D9DH STN01 CHR RAW MOLES ETHANE Float (MSB 1st) 0.000000
07583 1D9FH STN01 CHR RAW MISC BTU DRY Float (MSB 1st) 0.000000
07585 1DA1H STN01 CHR RAW MISC BTU SAT Float (MSB 1st) 0.000000
07587 1DA3H STN01 CHR RAW MISC SG Float (MSB 1st) 0.000000
07589 1DA5H STN01 CHR RAW MISC COMPRESSIBILITY Float (MSB 1st) 0.000000
07591 1DA7H STN01 CHR RAW MISC WOBBE INDEX Float (MSB 1st) 0.000000
07593 1DA9H STN01 CHR RAW MISC TOTAL UNNORM Float (MSB 1st) 0.000000
07595 1DABH STN01 CHR RAW MISC MOLAR MAS Float (MSB 1st) 0.000000
07597 1DADH STN01 KEYPAD MOLES NITROGEN Float (MSB 1st) 0.396900
07599 1DAFH STN01 KEYPAD MOLES CO2 Float (MSB 1st) 3.897900
07601 1DB1H STN01 KEYPAD MOLES H2S Float (MSB 1st) 0.000000
07603 1DB3H STN01 KEYPAD MOLES H2O Float (MSB 1st) 0.000000
07605 1DB5H STN01 KEYPAD MOLES METHANE Float (MSB 1st) 88.771000
07607 1DB7H STN01 KEYPAD MOLES ETHANE Float (MSB 1st) 3.957300
07609 1DB9H STN01 KEYPAD MOLES PROPANE Float (MSB 1st) 1.904500
07611 1DBBH STN01 KEYPAD MOLES N_BUTANE Float (MSB 1st) 0.389100
07613 1DBDH STN01 KEYPAD MOLES I_BUTANE Float (MSB 1st) 0.320100
07615 1DBFH STN01 KEYPAD MOLES N_PENTANE Float (MSB 1st) 0.089100
07617 1DC1H STN01 KEYPAD MOLES I_PENTANE Float (MSB 1st) 0.139500
07619 1DC3H STN01 KEYPAD MOLES HEXANE Float (MSB 1st) 0.134600
07621 1DC5H STN01 KEYPAD MOLES TOTAL Float (MSB 1st) 100.000000
07623 1DC7H STN01 CHR K_ACCEPT VALUE Float (MSB 1st) 0
07625 1DC9H STN01 GC INT 9026 RUN TIME Float (MSB 1st) 0
07627 1DCBH STN01 GC INT 9026 CURRENT STREAM Float (MSB 1st) 0
07629 1DCDH STN01 GC INT 9026 GC MODE Float (MSB 1st) 0
07631 1DCFH STN01 GC INT 9026 CALIBRATING Float (MSB 1st) 0
07633 1DD1H STN01 GC INT 9026 ACTIVE ALM Float (MSB 1st) 0
07635 1DD3H STN01 GC INT 9026 UNACK ALARM Float (MSB 1st) 0
07637 1DD5H STR01 MAINT MODE VALUE Float (MSB 1st) 0
07639 1DD7H STR01 STATUS VALUE Float (MSB 1st) 1
07641 1DD9H STR02 MAINT MODE VALUE Float (MSB 1st) 0
07643 1DDBH STR02 STATUS VALUE Float (MSB 1st) 2
07645 1DDDH STR01 PREV PRESS HOURLY IK Float (MSB 1st) 120.000000
07647 1DDFH STR01 PREV TEMP HOURLY IK Float (MSB 1st) 82.000000
07649 1DE1H STR01 PREV DPT HOURLY IK Float (MSB 1st) 25.000000
07651 1DE3H STR01 PREV GHV HOURLY IK Float (MSB 1st) 1058.365671
07653 1DE5H STR01 PREV UVOL FR HOURLY IK Float (MSB 1st) 160.934619
07655 1DE7H STR01 PREV CVOL FR HOURLY IK Float (MSB 1st) 1437.508029
07657 1DE9H STR01 PREV ENERGY FR HOURLY IK Float (MSB 1st) 1521.409149
07659 1DEBH STR01 PREV WOBBEINDEX HOURLY IK Float (MSB 1st) 1316.391297
07661 1DEDH STR01 PREV BASE DENS HOURLY IK Float (MSB 1st) 0.049758
07663 1DEFH STR01 PREV LINE DENS HOURLY IK Float (MSB 1st) 0.444454
07665 1DF1H STR01 PREV BASE COMP HOURLY IK Float (MSB 1st) 0.997460
07667 1DF3H STR01 PREV LINE COMP HOURLY IK Float (MSB 1st) 0.979916
07669 1DF5H STR01 PREV SG HOURLY IK Float (MSB 1st) 0.650189
07671 1DF7H STR01 PREV PRESS DAILY IK Float (MSB 1st) 0.000000
07673 1DF9H STR01 PREV TEMP DAILY IK Float (MSB 1st) 0.000000
07675 1DFBH STR01 PREV DPT DAILY IK Float (MSB 1st) 0.000000
07677 1DFDH STR01 PREV GHV DAILY IK Float (MSB 1st) 0.000000
07679 1DFFH STR01 PREV UVOL FR DAILY IK Float (MSB 1st) 0.000000
07681 1E01H STR01 PREV CVOL FR DAILY IK Float (MSB 1st) 0.000000
07683 1E03H STR01 PREV ENERGY FR DAILY IK Float (MSB 1st) 0.000000
07685 1E05H STR01 PREV WOBBEINDEX DAILY IK Float (MSB 1st) 0.000000
07687 1E07H STR01 PREV BASE DENS DAILY IK Float (MSB 1st) 0.000000
07689 1E09H STR01 PREV LINE DENS DAILY IK Float (MSB 1st) 0.000000
07691 1E0BH STR01 PREV BASE COMP DAILY IK Float (MSB 1st) 0.000000
07693 1E0DH STR01 PREV LINE COMP DAILY IK Float (MSB 1st) 0.000000
07695 1E0FH STR01 PREV SG DAILY IK Float (MSB 1st) 0.000000
07697 1E11H STR01 PREV PRESS MONTHLY IK Float (MSB 1st) 0.000000
07699 1E13H STR01 PREV TEMP MONTHLY IK Float (MSB 1st) 0.000000
07701 1E15H STR01 PREV DPT MONTHLY IK Float (MSB 1st) 0.000000
07703 1E17H STR01 PREV GHV MONTHLY IK Float (MSB 1st) 0.000000
07705 1E19H STR01 PREV UVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07707 1E1BH STR01 PREV CVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07709 1E1DH STR01 PREV ENERGY FR MONTHLY IK Float (MSB 1st) 0.000000
07711 1E1FH STR01 PREV WOBBEINDEX MONTHLY IK Float (MSB 1st) 0.000000
07713 1E21H STR01 PREV BASE DENS MONTHLY IK Float (MSB 1st) 0.000000
07715 1E23H STR01 PREV LINE DENS MONTHLY IK Float (MSB 1st) 0.000000
07717 1E25H STR01 PREV BASE COMP MONTHLY IK Float (MSB 1st) 0.000000
07719 1E27H STR01 PREV LINE COMP MONTHLY IK Float (MSB 1st) 0.000000
07721 1E29H STR01 PREV SG MONTHLY IK Float (MSB 1st) 0.000000
07723 1E2BH STR02 PREV PRESS HOURLY IK Float (MSB 1st) 0.000000
07725 1E2DH STR02 PREV TEMP HOURLY IK Float (MSB 1st) 0.000000
07727 1E2FH STR02 PREV DPT HOURLY IK Float (MSB 1st) 0.000000
07729 1E31H STR02 PREV GHV HOURLY IK Float (MSB 1st) 0.000000
07731 1E33H STR02 PREV UVOL FR HOURLY IK Float (MSB 1st) 0.000000
07733 1E35H STR02 PREV CVOL FR HOURLY IK Float (MSB 1st) 0.000000
07735 1E37H STR02 PREV ENERGY FR HOURLY IK Float (MSB 1st) 0.000000
07737 1E39H STR02 PREV WOBBEINDEX HOURLY IK Float (MSB 1st) 0.000000
07739 1E3BH STR02 PREV BASE DENS HOURLY IK Float (MSB 1st) 0.000000
07741 1E3DH STR02 PREV LINE DENS HOURLY IK Float (MSB 1st) 0.000000
07743 1E3FH STR02 PREV BASE COMP HOURLY IK Float (MSB 1st) 0.000000
07745 1E41H STR02 PREV LINE COMP HOURLY IK Float (MSB 1st) 0.000000
07747 1E43H STR02 PREV SG HOURLY IK Float (MSB 1st) 0.000000
07749 1E45H STR02 PREV PRESS DAILY IK Float (MSB 1st) 0.000000
07751 1E47H STR02 PREV TEMP DAILY IK Float (MSB 1st) 0.000000
07753 1E49H STR02 PREV DPT DAILY IK Float (MSB 1st) 0.000000
07755 1E4BH STR02 PREV GHV DAILY IK Float (MSB 1st) 0.000000
07757 1E4DH STR02 PREV UVOL FR DAILY IK Float (MSB 1st) 0.000000
07759 1E4FH STR02 PREV CVOL FR DAILY IK Float (MSB 1st) 0.000000
07761 1E51H STR02 PREV ENERGY FR DAILY IK Float (MSB 1st) 0.000000
07763 1E53H STR02 PREV WOBBEINDEX DAILY IK Float (MSB 1st) 0.000000
07765 1E55H STR02 PREV BASE DENS DAILY IK Float (MSB 1st) 0.000000
07767 1E57H STR02 PREV LINE DENS DAILY IK Float (MSB 1st) 0.000000
07769 1E59H STR02 PREV BASE COMP DAILY IK Float (MSB 1st) 0.000000
07771 1E5BH STR02 PREV LINE COMP DAILY IK Float (MSB 1st) 0.000000
07773 1E5DH STR02 PREV SG DAILY IK Float (MSB 1st) 0.000000
07775 1E5FH STR02 PREV PRESS MONTHLY IK Float (MSB 1st) 0.000000
07777 1E61H STR02 PREV TEMP MONTHLY IK Float (MSB 1st) 0.000000
07779 1E63H STR02 PREV DPT MONTHLY IK Float (MSB 1st) 0.000000
07781 1E65H STR02 PREV GHV MONTHLY IK Float (MSB 1st) 0.000000
07783 1E67H STR02 PREV UVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07785 1E69H STR02 PREV CVOL FR MONTHLY IK Float (MSB 1st) 0.000000
07787 1E6BH STR02 PREV ENERGY FR MONTHLY IK Float (MSB 1st) 0.000000
07789 1E6DH STR02 PREV WOBBEINDEX MONTHLY IK Float (MSB 1st) 0.000000
07791 1E6FH STR02 PREV BASE DENS MONTHLY IK Float (MSB 1st) 0.000000
07793 1E71H STR02 PREV LINE DENS MONTHLY IK Float (MSB 1st) 0.000000
07795 1E73H STR02 PREV BASE COMP MONTHLY IK Float (MSB 1st) 0.000000
07797 1E75H STR02 PREV LINE COMP MONTHLY IK Float (MSB 1st) 0.000000
07799 1E77H STR02 PREV SG MONTHLY IK Float (MSB 1st) 0.000000
07801 1E79H STR01 GCFWA HOURLY NITROGEN Float (MSB 1st) 0.396900
07803 1E7BH STR01 GCFWA HOURLY CO2 Float (MSB 1st) 3.897900
07805 1E7DH STR01 GCFWA HOURLY METHANE Float (MSB 1st) 88.771000
07807 1E7FH STR01 GCFWA HOURLY ETHANE Float (MSB 1st) 3.957300
07809 1E81H STR01 GCFWA HOURLY PROPANE Float (MSB 1st) 1.904500
07811 1E83H STR01 GCFWA HOURLY N_BUTANE Float (MSB 1st) 0.389100
07813 1E85H STR01 GCFWA HOURLY I_BUTANE Float (MSB 1st) 0.320100
07815 1E87H STR01 GCFWA HOURLY N_PENTANE Float (MSB 1st) 0.089100
07817 1E89H STR01 GCFWA HOURLY I_PENTANE Float (MSB 1st) 0.139500
07819 1E8BH STR01 GCFWA HOURLY HEXANE Float (MSB 1st) 0.134600
07821 1E8DH STR01 GCFWA HOURLY TOTAL Float (MSB 1st) 100.000000
07823 1E8FH STR02 GCFWA DAILY NITROGEN Float (MSB 1st) 0.000000
07825 1E91H STR02 GCFWA DAILY CO2 Float (MSB 1st) 0.000000
07827 1E93H STR02 GCFWA DAILY METHANE Float (MSB 1st) 0.000000
07829 1E95H STR02 GCFWA DAILY ETHANE Float (MSB 1st) 0.000000
07831 1E97H STR02 GCFWA DAILY PROPANE Float (MSB 1st) 0.000000
07833 1E99H STR02 GCFWA DAILY N_BUTANE Float (MSB 1st) 0.000000
07835 1E9BH STR02 GCFWA DAILY I_BUTANE Float (MSB 1st) 0.000000
07837 1E9DH STR02 GCFWA DAILY N_PENTANE Float (MSB 1st) 0.000000
07839 1E9FH STR02 GCFWA DAILY I_PENTANE Float (MSB 1st) 0.000000
07841 1EA1H STR02 GCFWA DAILY HEXANE Float (MSB 1st) 0.000000
07843 1EA3H STR02 GCFWA DAILY TOTAL Float (MSB 1st) 0.000000
07845 1EA5H STR02 GCFWA MONTHLY NITROGEN Float (MSB 1st) 0.000000
07847 1EA7H STR02 GCFWA MONTHLY CO2 Float (MSB 1st) 0.000000
07849 1EA9H STR02 GCFWA MONTHLY METHANE Float (MSB 1st) 0.000000
07851 1EABH STR02 GCFWA MONTHLY ETHANE Float (MSB 1st) 0.000000
07853 1EADH STR02 GCFWA MONTHLY PROPANE Float (MSB 1st) 0.000000
07855 1EAFH STR02 GCFWA MONTHLY N_BUTANE Float (MSB 1st) 0.000000
07857 1EB1H STR02 GCFWA MONTHLY I_BUTANE Float (MSB 1st) 0.000000
07859 1EB3H STR02 GCFWA MONTHLY N_PENTANE Float (MSB 1st) 0.000000
07861 1EB5H STR02 GCFWA MONTHLY I_PENTANE Float (MSB 1st) 0.000000
07863 1EB7H STR02 GCFWA MONTHLY HEXANE Float (MSB 1st) 0.000000
07865 1EB9H STR02 GCFWA MONTHLY TOTAL Float (MSB 1st) 0.000000
07867 1EBBH TIME AND DATE CUR.YEAR Float (MSB 1st) 2025
07869 1EBDH TIME AND DATE CUR.MONTH Float (MSB 1st) 7
07871 1EBFH TIME AND DATE CUR.DAY Float (MSB 1st) 21
07873 1EC1H TIME AND DATE CUR.HOUR Float (MSB 1st) 21
07875 1EC3H TIME AND DATE CUR.MINUTE Float (MSB 1st) 10
07877 1EC5H TIME AND DATE CUR.SECOND Float (MSB 1st) 59
07879 1EC7H TIME AND DATE DLOAD YEAR Float (MSB 1st) 2025
07881 1EC9H TIME AND DATE DLOAD MONTH Float (MSB 1st) 7
07883 1ECBH TIME AND DATE DLOAD DAY Float (MSB 1st) 21
07885 1ECDH TIME AND DATE DLOAD HOUR Float (MSB 1st) 20
07887 1ECFH TIME AND DATE DLOAD MINUTE Float (MSB 1st) 55
07889 1ED1H TIME AND DATE DLOAD SECOND Float (MSB 1st) 19
07891 1ED3H DLOAD TIME ACCEPT VALUE Float (MSB 1st) 0
07893 1ED5H SYS PEER STAT OUTPUT Float (MSB 1st) 0
07895 1ED7H SYS PEER STAT INPUT Float (MSB 1st) 3
07897 1ED9H STN01 GC INT 9026 RUN TIME Float (MSB 1st) 0
07899 1EDBH STN01 GC INT 9026 CURRENT STREAM Float (MSB 1st) 0
07901 1EDDH STN01 GC INT 9026 GC MODE Float (MSB 1st) 0
07903 1EDFH STN01 GC INT 9026 CALIBRATING Float (MSB 1st) 0
07905 1EE1H STN01 GC INT 9026 ACTIVE ALM Float (MSB 1st) 0
07907 1EE3H STN01 GC INT 9026 UNACK ALARM Float (MSB 1st) 0
07909 1EE5H SDV VLV OUTPUT Float (MSB 1st) 0
07911 1EE7H SDV VLV INPUT Float (MSB 1st) 0
07913 1EE9H ESD BUTTON INPUT Float (MSB 1st) 1
07915 1EEBH PT-12501-04 HIHILIM Float (MSB 1st) 450.000000
07917 1EEDH PT-12501-04 HILIM Float (MSB 1st) 400.000000
07919 1EEFH PT-12501-04 LOLIM Float (MSB 1st) 60.000000
07921 1EF1H PT-12501-04 LOLOLIM Float (MSB 1st) 30.000000
07923 1EF3H PT-12501-05 HIHILIM Float (MSB 1st) 150.000000
07925 1EF5H PT-12501-05 HILIM Float (MSB 1st) 120.000000
07927 1EF7H PT-12501-05 LOLIM Float (MSB 1st) 50.000000
07929 1EF9H PT-12501-05 LOLOLIM Float (MSB 1st) 25.000000
07931 1EFBH STN01 CVOL FR RAW Float (MSB 1st) 1437.508029
07933 1EFDH STN01 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07935 1EFFH STN01 CVOL FR HISCALE Float (MSB 1st) 5000.000000
07937 1F01H STR01 CVOL FR RAW Float (MSB 1st) 1437.508029
07939 1F03H STR01 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07941 1F05H STR01 CVOL FR HISCALE Float (MSB 1st) 5000.000000
07943 1F07H STR02 CVOL FR RAW Float (MSB 1st) 0.000000
07945 1F09H STR02 CVOL FR LOSCALE Float (MSB 1st) 0.000000
07947 1F0BH STR02 CVOL FR HISCALE Float (MSB 1st) 5000.000000
07949 1F0DH ESD BUTTON OUTPUT Float (MSB 1st) 1